{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["线路间隔","XX间隔"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"线路间隔","index":0,"n_rows":207,"n_cols":12,"rows_kept":207,"cut":false,"hidden":false,"merged":[[30,6,35,6],[36,6,42,6],[114,6,116,6],[117,6,120,6]]}
["序号","间隔名称","接收装置类型名称","接收装置类型编码","接收端子描述","接收端子匹配关键词","设计描述","信号类型","发送装置类型","发送装置类型编码","发送端子描述","发送端子匹配关键词"]
[1,"线路间隔","保护装置","PL","跳闸位置_GOOSE/合闸位置1_GOOSE",null,"断路器位置","<- GOOSE <-","智能终端","IL","断路器位置","断路器位置"]
[2,"线路间隔","保护装置","PL","合后位置_GOOSE",null,"闭锁重合闸","<- GOOSE <-","智能终端","IL","闭锁重合闸","闭锁、重合闸"]
[3,"线路间隔","保护装置","PL","合闸压力降低_GOOSE",null,"低气压（弹簧未储能）闭重","<- GOOSE <-","智能终端","IL"]
[4,"线路间隔","保护装置","PL","跳闸压力降低_GOOSE",null,"控制回路断线闭重","<- GOOSE <-","智能终端","IL"]
[5,"线路间隔","保护装置","PL","闭重1闭锁重合闸_GOOSE",null,"HWJ1","<- GOOSE <-","智能终端"]
[6,"线路间隔","保护装置","PL","闭重2闭锁重合闸_GOOSE",null,"HWJ2","<- GOOSE <-","智能终端"]
[7,"线路间隔","保护装置","PL","闭重3闭锁重合闸_GOOSE",null,"TWJ","<- GOOSE <-","智能终端"]
[8,"线路间隔","保护装置","PL","闭重4闭锁重合闸_GOOSE",null,"其他保护动作","<- GOOSE <-","智能终端"]
[9,"线路间隔","保护装置","PL","闭重5闭锁重合闸_GOOSE",null,"手合同期开入","<- GOOSE <-","智能终端"]
[10,"线路间隔","保护装置","PL","收相邻线_GOOSE",null,"双点遥信开入","<- GOOSE <-","智能终端"]
[11,"线路间隔","保护装置","PL","远跳1发远方跳闸_GOOSE",null,"单点遥信开入","<- GOOSE <-","智能终端"]
[12,"线路间隔","保护装置","PL","远跳2发远方跳闸_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[13,"线路间隔","保护装置","PL","远跳3发远方跳闸_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[14,"线路间隔","保护装置","PL","远跳4发远方跳闸_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[15,"线路间隔","保护装置","PL","远传1_1发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[16,"线路间隔","保护装置","PL","远传1_2发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[17,"线路间隔","保护装置","PL","远传1_3发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[18,"线路间隔","保护装置","PL","远传1_4发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[19,"线路间隔","保护装置","PL","远传1_5发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[20,"线路间隔","保护装置","PL","远传1_6发远传命令1_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[21,"线路间隔","保护装置","PL","远传2_1发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[22,"线路间隔","保护装置","PL","远传2_2发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[23,"线路间隔","保护装置","PL","远传2_3发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[24,"线路间隔","保护装置","PL","远传2_4发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[25,"线路间隔","保护装置","PL","远传2_5发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[26,"线路间隔","保护装置","PL","远传2_6发远传命令2_GOOSE",null,null,"<- GOOSE <-","智能终端"]
[27]
[28,"线路间隔","保护装置","PL",null,null,"检修状态遥信开入","<- GOOSE <-","智能终端"]
[29,"线路间隔","保护装置","PL","光纤1额定延迟时间","保护、电流","额定延时","<- SV <- ","合并单元","ML","保护电流","保护、电流"]
[30,"线路间隔","保护装置","PL","保护电流A相","保护、电压","保护电流","<- SV <- ","合并单元","ML","保护电压","保护、电压"]
[31,"线路间隔","保护装置","PL","启动电流A相",null,null,"<- SV <- ","合并单元"]
[32,"线路间隔","保护装置","PL","保护电流B相",null,null,"<- SV <- ","合并单元"]
[33,"线路间隔","保护装置","PL","启动电流B相",null,null,"<- SV <- ","合并单元"]
[34,"线路间隔","保护装置","PL","保护电流C相",null,null,"<- SV <- ","合并单元"]
[35,"线路间隔","保护装置","PL","启动电流C相",null,null,"<- SV <- ","合并单元"]
[36,"线路间隔","保护装置","PL","保护电压A相",null,"保护电压","<- SV <- ","合并单元"]
[37,"线路间隔","保护装置","PL","启动电压A相",null,null,"<- SV <- ","合并单元"]
[38,"线路间隔","保护装置","PL","保护电压B相",null,null,"<- SV <- ","合并单元"]
[39,"线路间隔","保护装置","PL","启动电压B相",null,null,"<- SV <- ","合并单元"]
[40,"线路间隔","保护装置","PL","保护电压C相",null,null,"<- SV <- ","合并单元"]
[41,"线路间隔","保护装置","PL","启动电压C相",null,null,"<- SV <- ","合并单元"]
[42,"线路间隔","保护装置","PL","同期电压",null,null,"<- SV <- ","合并单元"]
[43,"线路间隔","保护装置","PL"]
[null,"线路间隔","测控装置","CL",null,null,"断路器位置","<- GOOSE <-","智能终端","IL","断路器位置(辅助)"]
[null,"线路间隔","测控装置","CL",null,null,"双点遥信开入1\n（隔开开关1位置）","<- GOOSE <-","智能终端","IL","母线侧刀闸位置"]
[null,"线路间隔","测控装置","CL",null,null,"...","<- GOOSE <-","智能终端","IL","线路侧刀闸位置"]
[null,"线路间隔","测控装置","CL",null,null,"双点遥信开入8","<- GOOSE <-","智能终端","IL","避雷器刀闸位置"]
[11,"线路间隔","测控装置","CL",null,null,"单点遥信开入1","<- GOOSE <-","智能终端","IL","闸刀4位置（备用）","断路器位置"]
[12,"线路间隔","测控装置","CL",null,null,"...","<- GOOSE <-","智能终端","IL","断路器母线侧接地刀闸位置"]
[13,"线路间隔","测控装置","CL",null,null,"单点遥信开入8","<- GOOSE <-","智能终端","IL","断路器线路侧接地刀闸位置"]
[14,"线路间隔","测控装置","CL",null,null,"解除闭锁开入","<- GOOSE <-","智能终端","IL","避雷器接地刀闸位置"]
[15,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","线路快速接地刀闸位置"]
[16,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","装置检修（开入01)"]
[17,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器远控(开入02)"]
[18,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入14(手合/遥合/保护合)"]
[19,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入15(手跳/遥分)"]
[20,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器弹簧储能超时信号（开入33）"]
[21,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器合闸簧储能信号（开入34）"]
[22,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器气室补气报警（开入35）"]
[23,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","2气室补气报警（开入36）"]
[24,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","3气室补气报警（开入37）"]
[25,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","4气室补气报警（开入38）"]
[26,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","5气室补气报警（开入39）"]
[27,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","6气室补气报警（开入40）"]
[28,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器电机断电信号（开入41）"]
[29,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","隔离接地开关操作断电信号（开入42）"]
[30,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","辅助回路断电信号（开入43）"]
[31,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","驱潮加热回路断电信号（开入44）"]
[32,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","手投驱潮加热回路断电信号（开入45）"]
[33,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器低气压闭锁信号（开入46）"]
[34,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","信号及指示回路断电信号（开入47）"]
[35,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器近控信号（开入48）"]
[36,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","断路器远控信号（开入49）"]
[37,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","隔离接地近控信号（开入50）"]
[38,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","联锁解除信号（开入51）"]
[39,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","合闸簧未储能信号（开入52）"]
[40,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","合闸簧已储能信号（开入53）"]
[41,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","带电显示故障信号（开入54）"]
[42,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","A相有电信号（开入55）"]
[43,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","A相无电信号（开入56）"]
[44,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","C相有电信号（开入57）"]
[45,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","C相无电信号（开入58）"]
[46,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","TVA 0.2二次断电信号（开入59）"]
[47,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","TVA 0.2二次断电信号（开入62）"]
[48,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","TVA 3P二次断电信号（开入63）"]
[49,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","智能稳控系统报警信号（开入64）"]
[50,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入65（备用）"]
[51,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","合并单元对时信号异常（开入66）"]
[52,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","合并单元装置故障（开入67）"]
[53,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入68（备用）"]
[54,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入69（备用）"]
[55,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入70（备用）"]
[56,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入71（备用）"]
[57,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入72（备用）"]
[58,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入73（备用）"]
[59,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","开入74（备用）"]
[60,"线路间隔","测控装置","CL",null,null,"手合同期开入","<- GOOSE <-","智能终端","IL","开入75（备用）"]
[61,"线路间隔","测控装置","CL",null,null,"检修状态开入","<- GOOSE <-","智能终端","IL","开入76（备用）"]
[62,"线路间隔","测控装置",{"$nulls":4},"<- GOOSE <-","智能终端","IL","校时同步异常"]
[63,"线路间隔","测控装置",{"$nulls":4},"<- GOOSE <-","智能终端","IL","控回断线"]
[64,"线路间隔","测控装置",{"$nulls":4},"<- GOOSE <-","智能终端","IL","事故总"]
[65,"线路间隔","测控装置","CL",null,null,"GOOSE直流亮输入1","<- GOOSE <-","智能终端","IL","直流01"]
[66,"线路间隔","测控装置","CL",null,null,"GOOSE直流量输入20","<- GOOSE <-","智能终端","IL","直流02"]
[67,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL"]
[68,"线路间隔","测控装置","CL",null,null,null,"<- GOOSE <-","智能终端","IL","双点遥信开入N"]
[69,"线路间隔","测控装置","CL","单点遥信1",null,null,"<- GOOSE <-","合并单元","ML","采样异常","报警、告警"]
[70,"线路间隔","测控装置","CL","单点遥信2",null,null,"<- GOOSE <-","合并单元","ML","同步异常"]
[71,"线路间隔","测控装置","CL","单点遥信3",null,null,"<- GOOSE <-","合并单元","ML","装置自检异常"]
[72,"线路间隔","测控装置","CL","单点遥信4",null,null,"<- GOOSE <-","合并单元","ML","同步信号中断"]
[73,"线路间隔","测控装置",null,"单点遥信5",null,null,"<- GOOSE <-","合并单元","ML","MU接收品质无效"]
[74,"线路间隔","测控装置",null,"单点遥信6",null,null,"<- GOOSE <-","合并单元","ML","MU发送品质无效"]
[75,"线路间隔","测控装置",null,"单点遥信7",null,null,"<- GOOSE <-","合并单元","ML","MU接收检修不一致"]
[76,"线路间隔","测控装置",null,"单点遥信8",null,null,"<- GOOSE <-","合并单元","ML","检修状态"]
[77,"线路间隔","测控装置","CL","间隔1A相测量电流","测量|计量、电压","测量电流","<- SV <- ","合并单元","ML","电压","测量|计量、电压"]
[78,"线路间隔","测控装置","CL","间隔1B相测量电流","测量|计量、电流",null,"<- SV <- ","合并单元","ML","电流","测量|计量、电流"]
[79,"线路间隔","测控装置",null,"间隔1C相测量电流",null,null,"<- SV <- "]
[80,"线路间隔","测控装置",null,"间隔1A相电压",null,"测量电压","<- SV <- "]
[81,"线路间隔","测控装置",null,"间隔1B相电压",null,null,"<- SV <- "]
[82,"线路间隔","测控装置",null,"间隔1C相电压",null,null,"<- SV <- "]
[83,"线路间隔","测控装置",null,"间隔1同期抽取电压",null,null,"<- SV <- "]
[1,"线路间隔","智能终端","CL","跳闸",null,"...","<- GOOSE <-","线路保护","PL","跳闸1"]
[2,"线路间隔","智能终端","CL",null,null,"保护跳闸","<- GOOSE <-","智能终端","PL","跳闸2"]
[3,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸3"]
[4,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸4"]
[5,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸5"]
[6,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸6"]
[7,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸7"]
[8,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸8"]
[9,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸9"]
[10,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","跳闸10"]
[11,"线路间隔","智能终端","CL","合闸",null,"重合闸","<- GOOSE <-","智能终端","PL","重合1"]
[12,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","重合2"]
[13,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","闭重1"]
[14,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","PL","闭重2"]
[15,"线路间隔","智能终端","CL",null,null,"其他保护动作（闭锁重合闸）","<- GOOSE <-","母线保护","PM","闭重三跳1"]
[16,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","IL","闭重三跳2"]
[17,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","IL","闭重三跳3"]
[18,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","IL","闭重三跳4"]
[19,"线路间隔","智能终端","CL",null,null,null,"<- GOOSE <-","智能终端","IL","闭重三跳5"]
[20,"线路间隔","智能终端","CL","CJ05控制(DL遥跳)",null,"断路器手合GOOSE命令","<- GOOSE <-","测控装置","CL","断路器遥分"]
[21,"线路间隔","智能终端","CL","CJ02控制(DL遥合)",null,"断路器手分","<- GOOSE <-","测控装置","CL","断路器遥合"]
[22,"线路间隔","智能终端","CL","CJ08控制(G1允许)",null,"隔离刀闸合","<- GOOSE <-","测控装置","CL","母线侧刀闸控制"]
[23,"线路间隔","智能终端","CL","CJ06控制(G1遥分)",null,"隔离刀闸分","<- GOOSE <-","测控装置","CL","母线侧刀闸遥分"]
[24,"线路间隔","智能终端","CL","CJ07控制(G1遥合)",null,"地刀合","<- GOOSE <-","测控装置","CL","母线侧刀闸遥合"]
[25,"线路间隔","智能终端","CL","CJ11控制(G2允许)",null,"地刀分","<- GOOSE <-","测控装置","CL","线路侧刀闸控制"]
[26,"线路间隔","智能终端","CL","CJ09控制(G2遥分)",null,null,"<- GOOSE <-","测控装置","CL","线路侧刀闸遥分"]
[27,"线路间隔","智能终端","CL","CJ10控制(G2遥合)",null,null,"<- GOOSE <-","测控装置","CL","线路侧刀闸遥合"]
[28,"线路间隔","智能终端","CL","CJ14控制(G3允许)",null,null,"<- GOOSE <-","测控装置","CL","避雷器刀闸控制"]
[29,"线路间隔","智能终端","CL","CJ12控制(G3遥分)",null,null,"<- GOOSE <-","测控装置","CL","避雷器刀闸遥分"]
[30,"线路间隔","智能终端","CL","CJ13控制(G3遥合)",null,null,"<- GOOSE <-","测控装置","CL","避雷器刀闸遥合"]
[31,"线路间隔","智能终端","CL","CJ20控制(GD1允许)",null,null,"<- GOOSE <-","测控装置","CL","断路器母线侧接地刀闸控制"]
[32,"线路间隔","智能终端","CL","CJ18控制(GD1遥分)",null,null,"<- GOOSE <-","测控装置","CL","断路器母线侧接地刀闸遥分"]
[33,"线路间隔","智能终端","CL","CJ19控制(GD1遥合)",null,null,"<- GOOSE <-","测控装置","CL","断路器母线侧接地刀闸遥合"]
[34,"线路间隔","智能终端","CL","CJ23控制(GD2允许)",null,null,"<- GOOSE <-","测控装置","CL","断路器线路侧接地刀闸控制"]
[35,"线路间隔","智能终端","CL","CJ21控制(GD2遥分)",null,null,"<- GOOSE <-","测控装置","CL","断路器线路侧接地刀闸遥分"]
[36,"线路间隔","智能终端","CL","CJ22控制(GD2遥合)",null,null,"<- GOOSE <-","测控装置","CL","断路器线路侧接地刀闸遥合"]
[37,"线路间隔","智能终端","CL","CJ26控制(GD3允许)",null,null,"<- GOOSE <-","测控装置","CL","避雷器接地刀闸控制"]
[38,"线路间隔","智能终端","CL","CJ24控制(GD3遥分)",null,null,"<- GOOSE <-","测控装置","CL","避雷器接地刀闸遥合"]
[39,"线路间隔","智能终端","CL","CJ25控制(GD3遥合)",null,null,"<- GOOSE <-","测控装置","CL","避雷器接地刀闸遥分"]
[40,"线路间隔","智能终端","CL","CJ29控制(GD4允许)",null,null,"<- GOOSE <-","测控装置","CL","线路快速接地刀闸控制"]
[41,"线路间隔","智能终端","CL","CJ27控制(GD4遥分)",null,null,"<- GOOSE <-","测控装置","CL","线路快速接地刀闸遥合"]
[42,"线路间隔","智能终端","CL","CJ28控制(GD4遥合)",null,null,"<- GOOSE <-","测控装置","CL","线路快速接地刀闸遥分"]
[43,"线路间隔","智能终端","CL","通讯复归",null,null,"<- GOOSE <-","测控装置","CL","汇控柜光子牌告警复归"]
[44,"线路间隔","智能终端","CL","智能终端远方复归",null,null,"<- GOOSE <-","测控装置","CL","CJ16控制(G4遥合)"]
[45,"线路间隔","智能终端","CL"]
[46,"线路间隔","智能终端","CL"]
[1,"线路间隔","合并单元","ML","额定延时1760us",null,"额定延时","<- SV <- ","I母线合并单元","MM","采样额定延迟时间800us"]
[2,"线路间隔","合并单元","ML","保护1A相电流1",null,"1母保护电压A相1","<- SV <- ","I母线合并单元","MM","I母保护/测量A相电压UA1"]
[3,"线路间隔","合并单元","ML","保护1A相电流2",null,"1母保护电压A相2","<- SV <- ","I母线合并单元","MM","I母保护/测量A相电压UA2"]
[4,"线路间隔","合并单元","ML","保护1B相电流1",null,"1母保护电压B相1","<- SV <- ","I母线合并单元","MM","I母保护/测量B相电压UB1"]
[5,"线路间隔","合并单元","ML","保护1B相电流2",null,"1母保护电压B相2","<- SV <- ","I母线合并单元","MM","I母保护/测量B相电压UB2"]
[6,"线路间隔","合并单元","ML","保护1C相电流1",null,"1母保护电压C相1","<- SV <- ","I母线合并单元","MM","I母保护/测量C相电压UC1"]
[7,"线路间隔","合并单元","ML","保护1C相电流2",null,"1母保护电压C相2","<- SV <- ","I母线合并单元","MM","I母保护/测量C相电压UC2"]
[8,"线路间隔","合并单元","ML","保护2A相电流1（备用）",null,"2母保护电压A相1","<- SV <- ","II母线合并单元","MM","II母保护/测量A相电压UA1"]
[9,"线路间隔","合并单元","ML","保护2A相电流2（备用）",null,"2母保护电压A相2","<- SV <- ","II母线合并单元","MM","II母保护/测量A相电压UA2"]
[10,"线路间隔","合并单元","ML","保护2B相电流1（备用）",null,"2母保护电压B相1","<- SV <- ","II母线合并单元","MM","II母保护/测量B相电压UB1"]
[11,"线路间隔","合并单元","ML","保护2B相电流2（备用）",null,"2母保护电压B相2","<- SV <- ","II母线合并单元","MM","II母保护/测量B相电压UB2"]
[12,"线路间隔","合并单元","ML","保护2C相电流1（备用）",null,"2母保护电压C相1","<- SV <- ","II母线合并单元","MM","II母保护/测量C相电压UC1"]
[13,"线路间隔","合并单元","ML","保护2C相电流2（备用）",null,"2母保护电压C相2","<- SV <- ","II母线合并单元","MM","II母保护/测量C相电压UC2"]
[14,"线路间隔","合并单元","ML","测量A相电流",null,"1母测量电压A相","<- SV <- "]
[15,"线路间隔","合并单元","ML","测量B相电流",null,"1母测量电压B相","<- SV <- "]
[16,"线路间隔","合并单元","ML","测量C相电流",null,"1母测量电压C相","<- SV <- "]
[17,"线路间隔","合并单元","ML","线路A相同期电压1",null,"2母测量电压A相","<- SV <- "]
[18,"线路间隔","合并单元","ML","线路A相同期电压2",null,"2母测量电压B相","<- SV <- "]
[19,"线路间隔","合并单元","ML","I母保护/测量A相电压1（级联）",null,"2母测量电压C相","<- SV <- "]
[20,"线路间隔","合并单元","ML","I母保护/测量A相电压2（级联）",null,null,"<- SV <- "]
[21,"线路间隔","合并单元","ML","I母保护/测量B相电压1（级联）",null,null,"<- SV <- "]
[22,"线路间隔","合并单元","ML","I母保护/测量B相电压2（级联）",null,null,"<- SV <- "]
[23,"线路间隔","合并单元","ML","I母保护/测量C相电压1（级联）",null,null,"<- SV <- "]
[24,"线路间隔","合并单元","ML","I母保护/测量C相电压2（级联）",null,null,"<- SV <- "]
[25,"线路间隔","合并单元","ML","零序电流I01（备用）",null,null,"<- SV <- "]
[26,"线路间隔","合并单元","ML","零序电流I02（备用）",null,null,"<- SV <- "]
[27,"线路间隔","合并单元","ML","零序电压1（备用）",null,null,"<- SV <- "]
[28,"线路间隔","合并单元","ML","零序电压2（备用）",null,null,"<- SV <- "]
[29,"线路间隔","合并单元","ML","计量A相电压（备用）",null,null,"<- SV <- "]
[30,"线路间隔","合并单元","ML","计量B相电压（备用）",null,null,"<- SV <- "]
[31,"线路间隔","合并单元","ML","计量C相电压（备用）",null,null,"<- SV <- "]
[32,"线路间隔","合并单元","ML","1#母线与2#母线开关位置",null,"母线1隔刀位置","<- GOOSE <-","智能终端","PL"]
[33,"线路间隔","合并单元","ML","2#母线与3#母线开关位置",null,"母线2隔刀位置","<- GOOSE <-","智能终端","PL"]
[34,"线路间隔","合并单元","ML","1#母线与2#母线刀闸1位置",null,"母联断路器位置","<- GOOSE <-","智能终端","PL"]
[35,"线路间隔","合并单元","ML","1#母线与2#母线刀闸2位置",null,"母联隔离刀闸1位置","<- GOOSE <-","智能终端","PL"]
[36,"线路间隔","合并单元","ML","2#母线与3#母线刀闸1位置",null,"母联隔离刀闸2位置","<- GOOSE <-","智能终端","PL"]
[37,"线路间隔","合并单元","ML","2#母线与3#母线刀闸2位置",null,null,"<- GOOSE <-","智能终端","PL"]
[38,"线路间隔","合并单元","ML","1#母线刀闸位置",null,null,"<- GOOSE <-","智能终端","PL"]
[39,"线路间隔","合并单元","ML","2#母线刀闸位置",null,null,"<- GOOSE <-","智能终端","PL"]
[40,"线路间隔","合并单元","ML",null,null,"远方复归","<- GOOSE <-","测控装置","CL"]

{"sheet":"XX间隔","index":1,"n_rows":2,"n_cols":11,"rows_kept":2,"cut":false,"hidden":false,"merged":[]}
["序号","间隔名称","接收装置类型名称","接收装置类型编码","接收端子描述","接收端子匹配关键词","信号类型","发送装置类型","发送装置类型编码","发送端子描述","发送端子匹配关键词"]
[1,{"$nulls":5},"GOOSE"]