{"text_format":"2","workbook":"xlsx","n_sheets":5,"sheets":["测控装置","保护装置","智能终端","合并单元","schema语法和数据模板"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"测控装置","index":0,"n_rows":111,"n_cols":6,"rows_kept":111,"cut":false,"hidden":false,"merged":[[0,0,0,5],[7,0,7,5],[14,0,14,5],[20,0,20,5],[26,0,26,5],[37,0,37,5],[43,0,43,5],[49,0,49,5],[56,0,56,5],[63,0,63,5],[70,0,70,5],[76,0,76,5],[82,0,82,5],[89,0,89,5],[96,0,96,5],[103,0,103,5]]}
["小金_160118.SCD-装置(CT2201)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CT2201","#1主变高压侧测控装置","XJEC","FCK-851B","测控","49208FF1"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","10121","error","IED(CT2201)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","17577","error","IED(CT2201)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","7815","error","IED(CT2201)中存储的CCD校验码(49208FF1)与实际校验码(19EF46EA)不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CT2202)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CT2202","#2主变高压侧测控装置","XJEC","FCK-851B","测控","DD9F13CD"]
["序号","行号","日期","校验结果内容","应用标准","标准条款"]
[1,"65959","error","IED(CT2202)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","73415","error","IED(CT2202)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","63653","error","IED(CT2202)中存储的CCD校验码(DD9F13CD)与实际校验码(553A95BE)不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CM2202)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CM2202","\"220kV II母测控装","XJEC","FCK-851B","测控","628155BB"]
["序号","行号","日期","校验结果内容","应用标准","标准条款"]
["1","135729","error","IED(CM2202)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","133880","error","IED(CM2202)中存储的CCD校验码(628155BB)与实际校验码(522C0CF9)不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CM2201)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CM2201","220kV I母测控装","XJEC","FCK-851B","测控","C561D9FF"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","121339","error","IED(CM2201)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","119490","error","IED(CM2201)中存储的CCD校验码(C561D9FF)与实际校验码(F43FD7A2)不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CL2202)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CL2202","220kV丹金II线265测控装置","XJEC","FCK-851B","测控","1655DFC7"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","531544","error","IED(CL2202)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["2","522961","error","IED(CL2202)中存储的CCD校验码(1655DFC7)与实际校验码(48DDF29F)不一致","GB/T 32890","5.3"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CL22021","220kV丹金I线266测控装置","XJEC","FCK-851B","测控","F0D04322"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","518797","error","IED(CL2201)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["2","510214","error","IED(CL2201)中存储的CCD校验码(F0D04322)与实际校验码(BC7AF1B8)不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CL2204)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CL2204","\"220kV备用线264测控装置","XJEC","FCK-851B","测控","F6649EFA"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","971882","error","IED(CL2204)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["2","963299","error","IED(CL2204)中存储的CCD校验码(F6649EFA)与实际校验码(39B10E0B)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CL2203)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CL2203","220kV木金线261测控装","XJEC","FCK-851B","测控",38731719]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","959135","error","IED(CL2203)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["2","950552","error","IED(CL2203)中存储的CCD校验码(38731719)与实际校验码(B4141320)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CF2201)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CF2201","220kV母联测控装置","XJEC","FCK-851B","测控","57FF595"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","537665","error","IED(CF2201)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","543649","error","IED(CF2201)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","535708","error","IED(CF2201)中存储的CCD校验码(57FF595A)与实际校验码(14B08B86)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CT1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CT1101","\"#1主变中压侧测控装置","XJEC","FCK-851B","测控","8F1F82D"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","24100","error","IED(CT1101)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","31556","error","IED(CT1101)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","21794","error","IED(CT1101)中存储的CCD校验码(8F1F82DA)与实际校验码(C3E07B3D)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CT1102)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CT1102","#2主变中压侧测控装置","XJEC","FCK-851B","测控","446AB96"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","79938","error","IED(CT1102)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","87394","error","IED(CT1102)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","77632","error","IED(CT1102)中存储的CCD校验码(446AB963)与实际校验码(B3E40A0E)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CM1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CM1101","110kV I母测控装置","XJEC","FCK-851B","测控","1EF0D0A4"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","150119","error","IED(CM1101)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","148270","error","IED(CM1101)中存储的CCD校验码(1EF0D0A4)与实际校验码(58C984AA)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CM1102)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CM1102","110kV II母测控装置","XJEC","FCK-851B","测控","B26D781"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","164509","error","IED(CM1102)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","162660","error","IED(CM1102)中存储的CCD校验码(B26D7816)与实际校验码(A101C0F0)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CTB01)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CTB01","#1主变本体测控装置","XJEC","FCK-851B","测控","F38058A1"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","52003","error","IED(CTB01)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","59459","error","IED(CTB01)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","49697","error","IED(CTB01)中存储的CCD校验码(F38058A1)与实际校验码(661CD579)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CTB02)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CTB02","#2主变本体测控装","XJEC","FCK-851B","测控","325251CC"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","107840","error","IED(CTB02)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","115296","error","IED(CTB02)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE2)成员FCDA个数544不能超过256","DL/T1873","10.2"]
["3","105534","error","IED(CTB02)中存储的CCD校验码(325251CC)与实际校验码(EF642B9A)不一致","GB/T 32890","5.3"]
[" 小金_160118.SCD-装置(CG01)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","927100","error","IED(CG01)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["2","925605","error","IED(CG01)中存储的CCD校验码(CED0E31E)与实际校验码(39DCF20E)不一致","GB/T 32890","5.3"]
["3","925604","waring","IED(CG01)名称不符合规范要求","智能变电站系统配置（SCD）文件技术规范\r\n附件2：智能站工程配置补充要求-20200824","DL/T 1873 8.2.2、\r\n补充要求 3.2.1"]
["4","927100","waring","IED(CG01)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)的appID(PROT/LLN0.GO_Gcb2)格式不符合规范","DL/T1873","10.2"]
[" 小金_160118.SCD-装置(CG02)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","934345","error","IED(CG02)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)的appID(PROT/LLN0.GO_Gcb2)与IED(CG01)中重复定义","Q_CSG1204059-2020","A.1.3 Ied6"]
["2","934345","error","IED(CG02)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)未配置网络参数","Q_CSG1204059-2020"]
["3","932850","error","IED(CG02)中存储的CCD校验码(C7D2F98A)与实际校验码(E36DD3B9)不一致","GB/T 32890","5.3"]
["4","932849","waring","IED(CG02)名称不符合规范要求","智能变电站系统配置（SCD）文件技术规范\r\n附件2：智能站工程配置补充要求-20200824","DL/T 1873 8.2.2、\r\n补充要求 3.2.1"]
["5","934345","waring","IED(CG02)中访问点(S1:站控层)下的LD(PROT)GOOSE控制块(GO_Gcb2)的appID(PROT/LLN0.GO_Gcb2)格式不符合规范","DL/T1873","10.2"]

{"sheet":"保护装置","index":1,"n_rows":228,"n_cols":6,"rows_kept":228,"cut":false,"hidden":false,"merged":[[0,0,0,5],[7,0,7,5],[12,0,12,5],[19,0,19,5],[24,0,24,5],[31,0,31,5],[57,0,57,5],[62,0,62,5],[68,0,68,5],[73,0,73,5],[79,0,79,5],[85,0,85,5],[91,0,91,5],[97,0,97,5],[103,0,103,5],[110,0,110,5],[116,0,116,5],[121,0,121,5],[130,0,130,5],[137,0,137,5],[144,0,144,5],[152,0,152,5],[159,0,159,5],[200,0,200,5],[207,0,207,5],[213,0,213,5],[220,0,220,5]]}
["  小金_160118.SCD-装置(PT2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PT2201A","1#变压器保护A","SZNARI","PRS-778-D","保护装置","2FA0C009"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["55","393014","error","IED(PT2201A)中存储的CCD校验码(2FA0C009)与实际校验码(C140B13A)不一致","GB/T 32890","5.3"]
["56","402318","waring","IED(PT2201A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb0)的appID(PT2201API/LLN0$GO$gocb0)格式不符合规范","DL/T1873","10.2"]
["57","402319","waring","IED(PT2201A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb1)的appID(PT2201API/LLN0$GO$gocb1)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PT2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PT2201B","1#变压器保护B","XJEC","WBH-801B","保护装置",{"$f":"MID(D12,24,8)","v":"F96B62E4"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","403659","error","IED(PT2201B)中存储的CCD校验码(F96B62E4)与实际校验码(3D1D465E)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PT2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PT2202A","2#变压器保护A","SZNARI","PRS-778-D","保护装置",{"$f":"MID(D17,24,8)","v":"02B3F456"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["55","416939","error","IED(PT2202A)中存储的CCD校验码(02B3F456)与实际校验码(9BBA94C2)不一致","GB/T 32890","5.3"]
["56","426243","waring","IED(PT2202A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb0)的appID(PT2202API/LLN0$GO$gocb0)格式不符合规范","DL/T1873","10.2"]
["57","426244","waring","IED(PT2202A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb1)的appID(PT2202API/LLN0$GO$gocb1)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PT2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PT2202B","2#变压器保护B","XJEC","WBH-801B","保护装置",{"$f":"MID(D24,24,8)","v":"4270D93D"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","427584","error","IED(PT2202B)中存储的CCD校验码(4270D93D)与实际校验码(218E224A)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PM2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PM2201A","220kV母线保护A","SZNARI","BP_2C_D","保护装置",{"$f":"MID(D29,24,8)","v":"52EC4FB6"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["96","738608","error","IED(PM2201A)中存储的CCD校验码(52EC4FB6)与实际校验码(E0810270)不一致","GB/T 32890","5.3"]
["97","748665","waring","IED(PM2201A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb0)的appID(PM2201AGOLD/LLN0$GO$gocb0)格式不符合规范","DL/T1873","10.2"]
["98","748666","waring","IED(PM2201A)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb1)的appID(PM2201API/LLN0$GO$gocb1)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PM2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PM2201B","220kV母线保护B","XJEC","WMH-800B","保护装置",{"$f":"MID(D57,24,8)","v":"210574EF"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","583237","error","IED(PM2201B)中访问点(G1:过程层GOOSE)下的LD(PI0)数据集(dsGOOSE3)成员FCDA个数308不能超过256","DL/T1873","10.2"]
["28","583719","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO9.SPCS211)外部虚端子(IED=PL2203B,addr=PI/RBRF8.Str.general)类型不一致","GB/T34121"]
["29","583719","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO9.SPCS211)bType类型(SPS)与关联外部虚端子(PL2203B PI/RBRF8.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["30","583720","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO9.SPCS212)外部虚端子(IED=PL2203B,addr=PI/RBRF9.Str.general)类型不一致","GB/T34121"]
["31","583720","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO9.SPCS212)bType类型(SPS)与关联外部虚端子(PL2203B PI/RBRF9.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["32","583721","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO9.SPCS213)外部虚端子(IED=PL2203B,addr=PI/RBRF10.Str.general)类型不一致","GB/T34121"]
["33","583721","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO9.SPCS213)bType类型(SPS)与关联外部虚端子(PL2203B PI/RBRF10.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["34","583722","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO9.DPCS42)外部虚端子(IED=IL2203B,addr=RPIT/XSWI1.Pos.stVal)类型不一致","GB/T34121"]
["35","583722","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO9.DPCS42)bType类型(DPS)与关联外部虚端子(IL2203B RPIT/XSWI1.Pos)的类型(Dbpos)不匹配","GB/T34121"]
["36","583723","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO9.DPCS43)外部虚端子(IED=IL2203B,addr=RPIT/XSWI2.Pos.stVal)类型不一致","GB/T34121"]
["37","583723","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO9.DPCS43)bType类型(DPS)与关联外部虚端子(IL2203B RPIT/XSWI2.Pos)的类型(Dbpos)不匹配","GB/T34121"]
["38","583724","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO10.SPCS216)外部虚端子(IED=PL2204B,addr=PI/RBRF8.Str.general)类型不一致","GB/T34121"]
["39","583724","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO10.SPCS216)bType类型(SPS)与关联外部虚端子(PL2204B PI/RBRF8.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["40","583725","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO10.SPCS217)外部虚端子(IED=PL2204B,addr=PI/RBRF9.Str.general)类型不一致","GB/T34121"]
["41","583725","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO10.SPCS217)bType类型(SPS)与关联外部虚端子(PL2204B PI/RBRF9.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["42","583726","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO10.SPCS218)外部虚端子(IED=PL2204B,addr=PI/RBRF10.Str.general)类型不一致","GB/T34121"]
["43","583726","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO10.SPCS218)bType类型(SPS)与关联外部虚端子(PL2204B PI/RBRF10.Str)的类型(BOOLEAN)不匹配","GB/T34121"]
["44","583727","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO10.DPCS44)外部虚端子(IED=IL2204B,addr=RPIT/XSWI1.Pos.stVal)类型不一致","GB/T34121"]
["45","583727","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO10.DPCS44)bType类型(DPS)与关联外部虚端子(IL2204B RPIT/XSWI1.Pos)的类型(Dbpos)不匹配","GB/T34121"]
["46","583728","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的关联内(PI0/GOINGGIO10.DPCS45)外部虚端子(IED=IL2204B,addr=RPIT/XSWI2.Pos.stVal)类型不一致","GB/T34121"]
["47","583728","error","IED(PM2201B)中访问点(G1:过程层GOOSE)中LD(PI0)的虚端子(PI0/GOINGGIO10.DPCS45)bType类型(DPS)与关联外部虚端子(IL2204B RPIT/XSWI2.Pos)的类型(Dbpos)不匹配","GB/T34121"]
["48","560688","error","IED(PM2201B)中存储的CCD校验码(210574EF)与实际校验码(D221ED02)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PL2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2202A","220kV丹金II线265保护A","南瑞继保","\"PCS-931GPM_120676_439FA927","保护装置",{"$f":"MID(D62,24,8)","v":"DE9A836A"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["21","475541","error","IED(PL2202A)中存储的CCD校验码(DE9A836A)与实际校验码(25097653)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PL2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2202B","220kV丹金II线265保护B","SF","CSC103BE","保护装置",{"$f":"MID(D67,24,8)","v":"95B6CB8E"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["22","494747","error","IED(PL2202B)中存储的CCD校验码(95B6CB8E)与实际校验码(1057E697)不一致","GB/T 32890","5.3"]
["23","504186","waring","IED(PL2202B)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL2202BPI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2201A","220kV丹金I线266保护A","南瑞继保","\"PCS-931GPM_120676_439FA927",null,{"$f":"MID(D73,24,8)","v":"C79DF0FB"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["21","440866","error","IED(PL2201A)中存储的CCD校验码(C79DF0FB)与实际校验码(AAC5B326)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PL2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2201B","220kV丹金I线266保护B","SF","CSC103BE","保护装置",{"$f":"MID(D78,24,8)","v":"44FCA164"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["22","460072","error","IED(PL2201B)中存储的CCD校验码(44FCA164)与实际校验码(FA6E3C8D)不一致","GB/T 32890","5.3"]
["23","469511","waring","IED(PL2201B)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL2201BPI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL2204A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2204A","220kV备用线264保护A","南瑞继保","PCS-931GPM-D","保护装置",{"$f":"MID(D84,24,8)","v":"F5BEFE28"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["21","987764","error","IED(PL2204A)中存储的CCD校验码(F5BEFE28)与实际校验码(425CFFD2)不一致","GB/T 32890","5.3"]
["22","997460","waring","IED(PL2204A)中访问点(G1:超高压线路保护装置)下的LD(PI1)GOOSE控制块(gocb0)的appID(PL2204API/LLN0.gocb0)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL2204B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2204B","220kV备用线264保护B","SF","CSC103BE","保护装置",{"$f":"MID(D90,24,8)","v":"0C18DE74"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["22","1014947","error","IED(PL2204B)中存储的CCD校验码(0C18DE74)与实际校验码(1A19A53D)不一致","GB/T 32890","5.3"]
["23","1024386","waring","IED(PL2204B)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL2204BPI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL2203A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2203A","220kV木金线261保护A","南瑞继保","PCS-931GPM-D","保护装置",{"$f":"MID(D96,24,8)","v":"28241AF6"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["21","976047","error","IED(PL2203A)中存储的CCD校验码(28241AF6)与实际校验码(3F188DBD)不一致","GB/T 32890","5.3"]
["22","985743","waring","IED(PL2203A)中访问点(G1:超高压线路保护装置)下的LD(PI1)GOOSE控制块(gocb0)的appID(PL2203API/LLN0.gocb0)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL2203B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL2203B","220kV木金线261保护B","SF","CSC103BE","保护装置",{"$f":"MID(D102,24,8)","v":"EE577919"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["22","999480","error","IED(PL2203B)中存储的CCD校验码(EE577919)与实际校验码(5CD817A0)不一致","GB/T 32890","5.3"]
["23","1008919","waring","IED(PL2203B)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL2203BPI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PF2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PF2201A","\"220kV丹金I线266保护A","南瑞继保","\"PCS-931GPM_120676_439FA927","保护装置",{"$f":"MID(D110,24,8)","v":"A4751CAA"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","551227","error","IED(PF2201A)中访问点(S1:断路器失灵起动及辅助保护装置)下的LD(RCD)数据集(dsRelayRec)FCDA成员(RCD/RDRE1.RcdMade)不存在","DL/T1873","10.2"]
["2","551228","error","IED(PF2201A)中访问点(S1:断路器失灵起动及辅助保护装置)下的LD(RCD)数据集(dsRelayRec)FCDA成员(RCD/RDRE1.FltNum)不存在","DL/T1873","10.2"]
["10","547654","error","IED(PF2201A)中存储的CCD校验码(A4751CAA)与实际校验码(83665960)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PF2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PF2201B","\"220kV丹金I线266保护B","SF","CSC103BE","保护装置",{"$f":"MID(D115,24,8)","v":"F2662DEE"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["8","552244","error","IED(PF2201B)中存储的CCD校验码(F2662DEE)与实际校验码(6E41D186)不一致","GB/T 32890","5.3"]
["9","556189","waring","IED(PF2201B)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PF2201BPI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PM1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PM1101","110kV母线保护","NRR","PCS-915GA-D_00112527","保护装置",{"$f":"MID(D121,23,8)","v":"6FE27D82"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["110","753986","error","IED(PM1101)中存储的CCD校验码(6FE27D82)与实际校验码(AD7C761A)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(PL1107)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1107","110kV兴金线168保测装置","SNR","PRS-713-D","保护装置",{"$f":"MID(D127,23,8)","v":"E1D32633"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1113405","error","IED(PL1107)中访问点(S1:常规mms服务功能)下的LD(CTRL)GOOSE控制块(gocb03)未配置网络参数","Q_CSG1204059-2020"]
["79","1112637","error","IED(PL1107)中存储的CCD校验码(E1D32633)与实际校验码(C8B33059)不一致","GB/T 32890","5.3"]
["80","1113405","waring","IED(PL1107)中访问点(S1:常规mms服务功能)下的LD(CTRL)GOOSE控制块(gocb03)的appID(PL1107CTRL/LLN0$GO$gocb03)格式不符合规范","DL/T1873","10.2"]
["81","1121549","waring","IED(PL1107)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb0)的appID(PL1107PI/LLN0$GO$gocb0)格式不符合规范","DL/T1873","10.2"]
["82","1121558","waring","IED(PL1107)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb1)的appID(PL1107PI/LLN0$GO$gocb1)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL1103)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1103","110kV固金线166保护","SF","CSC163AE","保护装置",{"$f":"MID(D135,23,8)","v":"F14CEC33"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["72","868741","error","IED(PL1103)中存储的CCD校验码(F14CEC33)与实际校验码(8AFCC869)不一致","GB/T 32890","5.3"]
["73","885113","waring","IED(PL1103)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL1103PI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["74","885114","waring","IED(PL1103)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBCtrl)的appID(PL1103PI/LLN0$GO$GoCBCtrl)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL1104)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1104","110kV备用线162保护","SF","CSC163AE","保护装置",{"$f":"MID(D142,23,8)","v":"31D746A5"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["72","897173","error","IED(PL1104)中存储的CCD校验码(31D746A5)与实际校验码(05C4401C)不一致","GB/T 32890","5.3"]
["73","913545","waring","IED(PL1104)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL1104PI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["74","913546","waring","IED(PL1104)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBCtrl)的appID(PL1104PI/LLN0$GO$GoCBCtrl)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1101","110kV备用线169保护","SF","CSC163AE","保护装置",{"$f":"MID(D149,23,8)","v":"C36A1284"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["73","811875","error","IED(PL1101)中存储的CCD校验码(C36A1284)与实际校验码(66CA2A49)不一致","GB/T 32890","5.3"]
["74","828248","waring","IED(PL1101)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL1101PI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["75","828249","waring","IED(PL1101)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBCtrl)的appID(PL1101PI/LLN0$GO$GoCBCtrl)格式不符合规范","DL/T1873","10.2"]
[]
["  小金_160118.SCD-装置(PL1102)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1102","110kV备用线170保护","SF","CSC163AE","保护装置",{"$f":"MID(D157,23,8)","v":"7BBD689F"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["73","840308","error","IED(PL1102)中存储的CCD校验码(7BBD689F)与实际校验码(A4030816)不一致","GB/T 32890","5.3"]
["74","856681","waring","IED(PL1102)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PL1102PI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["75","856682","waring","IED(PL1102)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBCtrl)的appID(PL1102PI/LLN0$GO$GoCBCtrl)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PL1105)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PL1105","110kV金艺线165保护测控装置","SNR","PRS-713-D","保护装置",{"$f":"MID(D198,23,8)","v":"F8CE7A8C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["62","1089686","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPATCTR1.Amp1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PATCTR1.Amp1)类型不一致","GB/T34121"]
["64","1089686","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPATCTR1.Amp1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PATCTR1.Amp1)的类型(SAV)不匹配","GB/T34121"]
["65","1089687","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPBTCTR2.Amp1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PBTCTR1.Amp1)类型不一致","GB/T34121"]
["67","1089687","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPBTCTR2.Amp1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PBTCTR1.Amp1)的类型(SAV)不匹配","GB/T34121"]
["68","1089688","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPCTCTR3.Amp1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PCTCTR1.Amp1)类型不一致","GB/T34121"]
["70","1089688","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPCTCTR3.Amp1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PCTCTR1.Amp1)的类型(SAV)不匹配","GB/T34121"]
["71","1089689","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPATVTR1.Vol1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UATVTR1.Vol1)类型不一致","GB/T34121"]
["73","1089689","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPATVTR1.Vol1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UATVTR1.Vol1)的类型(SAV)不匹配","GB/T34121"]
["74","1089690","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPBTVTR2.Vol1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UBTVTR1.Vol1)类型不一致","GB/T34121"]
["76","1089690","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPBTVTR2.Vol1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UBTVTR1.Vol1)的类型(SAV)不匹配","GB/T34121"]
["77","1089691","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPCTVTR3.Vol1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UCTVTR1.Vol1)类型不一致","GB/T34121"]
["79","1089691","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPCTVTR3.Vol1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UCTVTR1.Vol1)的类型(SAV)不匹配","GB/T34121"]
["80","1089692","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPLTVTR4.Vol1.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UXTVTR1.Vol1)类型不一致","GB/T34121"]
["82","1089692","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPLTVTR4.Vol1.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UXTVTR1.Vol1)的类型(SAV)不匹配","GB/T34121"]
["83","1089693","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPATCTR1.Amp2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PATCTR1.Amp2)类型不一致","GB/T34121"]
["85","1089693","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPATCTR1.Amp2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PATCTR1.Amp2)的类型(SAV)不匹配","GB/T34121"]
["86","1089694","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPBTCTR2.Amp2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PBTCTR1.Amp2)类型不一致","GB/T34121"]
["88","1089694","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPBTCTR2.Amp2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PBTCTR1.Amp2)的类型(SAV)不匹配","GB/T34121"]
["89","1089695","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPCTCTR3.Amp2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/PCTCTR1.Amp2)类型不一致","GB/T34121"]
["91","1089695","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPCTCTR3.Amp2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/PCTCTR1.Amp2)的类型(SAV)不匹配","GB/T34121"]
["92","1089696","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPATVTR1.Vol2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UATVTR1.Vol2)类型不一致","GB/T34121"]
["94","1089696","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPATVTR1.Vol2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UATVTR1.Vol2)的类型(SAV)不匹配","GB/T34121"]
["95","1089697","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPBTVTR2.Vol2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UBTVTR1.Vol2)类型不一致","GB/T34121"]
["97","1089697","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPBTVTR2.Vol2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UBTVTR1.Vol2)的类型(SAV)不匹配","GB/T34121"]
["98","1089698","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPCTVTR3.Vol2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UCTVTR1.Vol2)类型不一致","GB/T34121"]
["100","1089698","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPCTVTR3.Vol2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UCTVTR1.Vol2)的类型(SAV)不匹配","GB/T34121"]
["101","1089699","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPLTVTR4.Vol2.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/UXTVTR1.Vol2)类型不一致","GB/T34121"]
["103","1089699","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPLTVTR4.Vol2.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/UXTVTR1.Vol2)的类型(SAV)不匹配","GB/T34121"]
["104","1089700","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPATCTR4.Amp.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/MATCTR1.Amp)类型不一致","GB/T34121"]
["106","1089700","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPATCTR4.Amp.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/MATCTR1.Amp)的类型(SAV)不匹配","GB/T34121"]
["107","1089701","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPBTCTR5.Amp.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/MBTCTR1.Amp)类型不一致","GB/T34121"]
["109","1089701","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPBTCTR5.Amp.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/MBTCTR1.Amp)的类型(SAV)不匹配","GB/T34121"]
["110","1089702","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的关联内(SVLD/SVINPCTCTR6.Amp.instMag.i)外部虚端子(IED=ML1105,addr=MUSV01/MCTCTR1.Amp)类型不一致","GB/T34121"]
["112","1089702","error","IED(PL1105)中访问点(M1:SMV服务功能)中LD(SVLD)的虚端子(SVLD/SVINPCTCTR6.Amp.instMag.i)CDC类型(INT32)与关联外部虚端子(ML1105 MUSV01/MCTCTR1.Amp)的类型(SAV)不匹配","GB/T34121"]
["113","1079662","error","IED(PL1105)中存储的CCD校验码(F8CE7A8C)与实际校验码(B76144C4)不一致","GB/T 32890","5.3"]
["114","1087491","waring","IED(PL1105)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb0)的appID(PL1105PI/LLN0$GO$gocb0)格式不符合规范","DL/T1873","10.2"]
["115","1087492","waring","IED(PL1105)中访问点(G1:GOOSE服务功能)下的LD(PI)GOOSE控制块(gocb1)的appID(PL1105PI/LLN0$GO$gocb1)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(PF1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["PF1101","110kV母联保护","SF","CSC122ME","保护装置",{"$f":"MID(D205,23,8)","v":"F6333733"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["57","716923","error","IED(PF1101)中存储的CCD校验码(F6333733)与实际校验码(9003F145)不一致","GB/T 32890","5.3"]
["58","726916","waring","IED(PF1101)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBTrip)的appID(PF1101PI/LLN0$GO$GoCBTrip)格式不符合规范","DL/T1873","10.2"]
["59","726917","waring","IED(PF1101)中访问点(G1:)下的LD(PI)GOOSE控制块(GoCBCtrl)的appID(PF1101PI/LLN0$GO$GoCBCtrl)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(QJHW60)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["QJHW60","直流装置","Jhw","QJHW60","保护装置",{"$f":"MID(D213,23,8)","v":"D92B2B2D"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","948677","error","IED(QJHW60)中访问点(S1:)下的LD(DCPS)数据集(statusinfo)成员FCDA个数超过允许的最大值(当前数=59, 最大值=50)","DL/T1873","10.2"]
["2","948653","error","IED(QJHW60)中存储的CCD校验码(D92B2B2D)与实际校验码()不一致","GB/T 32890","5.3"]
["小金_160118.SCD-装置(CS1001)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CS1001","10kV站用变1","XJEC","WCB-822C","保护装置",{"$f":"MID(D219,23,8)","v":"B824978B"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","944317","error","IED(CS1001)中访问点(G1:过程层)下的LD(PI)GOOSE控制块(GO_Gcb1)未配置网络参数","Q_CSG1204059-2020"]
["2","940095","error","IED(CS1001)中存储的CCD校验码(B824978B)与实际校验码(BCFEA8E9)不一致","GB/T 32890","5.3"]
["3","944317","waring","IED(CS1001)中访问点(G1:过程层)下的LD(PI)GOOSE控制块(GO_Gcb1)的appID(PI/LLN0.GO_Gcb1)格式不符合规范","DL/T1873","10.2"]
["红房变-小金_160118.SCD-装置(CS1002)校验结果"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["CS1002","10kV站用变2","XJEC","WCB-822C","保护装置",{"$f":"MID(D227,23,8)","v":"796EE1DF"}]
["1","948596","error","IED(CS1002)中访问点(G1:过程层)下的LD(PI)GOOSE控制块(GO_Gcb1)的appID(PI/LLN0.GO_Gcb1)与IED(CS1001)中重复定义","Q_CSG1204059-2020","A.1.3 Ied6"]
["2","948596","error","IED(CS1002)中访问点(G1:过程层)下的LD(PI)GOOSE控制块(GO_Gcb1)未配置网络参数","Q_CSG1204059-2020"]
["3","944374","error","IED(CS1002)中存储的CCD校验码(796EE1DF)与实际校验码(A30A242F)不一致","GB/T 32890","5.3"]
["4","948596","waring","IED(CS1002)中访问点(G1:过程层)下的LD(PI)GOOSE控制块(GO_Gcb1)的appID(PI/LLN0.GO_Gcb1)格式不符合规范","DL/T1873","10.2"]

{"sheet":"智能终端","index":2,"n_rows":197,"n_cols":6,"rows_kept":197,"cut":false,"hidden":false,"merged":[[0,0,0,5],[5,0,5,5],[10,0,10,5],[15,0,15,5],[20,0,20,5],[25,0,25,5],[30,0,30,5],[35,0,35,5],[41,0,41,5],[46,0,46,5],[51,0,51,5],[56,0,56,5],[61,0,61,5],[66,0,66,5],[71,0,71,5],[76,0,76,5],[81,0,81,5],[86,0,86,5],[91,0,91,5],[96,0,96,5],[101,0,101,5],[106,0,106,5],[111,0,111,5],[122,0,122,5],[127,0,127,5],[132,0,132,5],[137,0,137,5],[142,0,142,5],[147,0,147,5],[152,0,152,5],[157,0,157,5],[162,0,162,5],[167,0,167,5],[172,0,172,5],[177,0,177,5],[182,0,182,5],[187,0,187,5],[192,0,192,5]]}
["  小金_160118.SCD-装置(IT2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT2201A","1#主变高压侧智能终端A","XJEC","DBU806","智能终端",{"$f":"MID(D5,24,8)","v":"5DA11603"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["33","212682","error","IED(IT2201A)中存储的CCD校验码(5DA11603)与实际校验码(C6FB7957)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT2201B","1#主变高压侧智能终端B","XJEC","DBU806","智能终端",{"$f":"MID(D10,24,8)","v":"9A192F95"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["5","221494","error","IED(IT2201B)中存储的CCD校验码(9A192F95)与实际校验码(D1AB3411)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT2202A","2#主变高压侧智能终端A","XJEC","DBU806","智能终端",{"$f":"MID(D15,24,8)","v":"011C9D9C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["33","282771","error","IED(IT2202A)中存储的CCD校验码(011C9D9C)与实际校验码(27636865)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT2202B","2#主变高压侧智能终端B","XJEC","DBU806","智能终端",{"$f":"MID(D20,24,8)","v":"D738614A"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["5","291583","error","IED(IT2202B)中存储的CCD校验码(D738614A)与实际校验码(C92A3837)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IM2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IM2201A","220kV I母线智能终端",null,"DBU816","智能终端",{"$f":"MID(D25,24,8)","v":"CE5AA102"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["13","353700","error","IED(IM2201A)中存储的CCD校验码(CE5AA102)与实际校验码(A38FDED2)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IM2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IM2201B","220kV II母线智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D30,24,8)","v":"D8509B09"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["13","361541","error","IED(IM2201B)中存储的CCD校验码(D8509B09)与实际校验码(40E85E54)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2201A","220kV丹金I线266智能终端A","XJEC","DBU806","智能终端",{"$f":"MID(D35,24,8)","v":"0A8ADE1D"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","589794","error","IED(IL2201A)中存储的CCD校验码(0A8ADE1D)与实际校验码(2BF1FEE6)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2201B","220kV丹金I线266智能终端B","XJEC","DBU806","智能终端",{"$f":"MID(D41,24,8)","v":"7BC3F36B"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["17","602780","error","IED(IL2201B)中访问点(G2:)下的LD(RPIT)GOOSE控制块(gocb9)未配置网络参数","Q_CSG1204059-2020"]
["18","602112","error","IED(IL2201B)中存储的CCD校验码(7BC3F36B)与实际校验码(20AFE274)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2202A","220kV丹金II线265智能终端A","XJEC","DBU806",null,{"$f":"MID(D46,24,8)","v":"DE2C8716"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","614418","error","IED(IL2202A)中存储的CCD校验码(DE2C8716)与实际校验码(4D2EEB0E)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2202B","220kV丹金II线265智能终端B","XJEC","DBU806",null,{"$f":"MID(D51,24,8)","v":"B4A8BB70"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["17","626736","error","IED(IL2202B)中存储的CCD校验码(B4A8BB70)与实际校验码(092217DD)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2203A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2203A","220kV木金线261智能终端A","XJEC","DBU806",null,{"$f":"MID(D56,24,8)","v":"652BE4D2"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","1044422","error","IED(IL2203A)中存储的CCD校验码(652BE4D2)与实际校验码(EFE201C5)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2203A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2203B","220kV木金线261智能终端B","XJEC","DBU806",null,{"$f":"MID(D61,24,8)","v":"652BE4D2"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","1044422","error","IED(IL2203A)中存储的CCD校验码(652BE4D2)与实际校验码(EFE201C5)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2204A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2204A","220kV备用线264智能终端A","XJEC","DBU806",null,{"$f":"MID(D66,24,8)","v":"96EC569E"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","1053238","error","IED(IL2204A)中存储的CCD校验码(96EC569E)与实际校验码(7D92CE46)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL2204B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL2204B","220kV备用线264智能终端A","XJEC","DBU806",null,{"$f":"MID(D71,24,8)","v":"8AEFFD55"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["17","1070858","error","IED(IL2204B)中存储的CCD校验码(8AEFFD55)与实际校验码(65A2720D)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IF2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IF2201A","220kV母联智能终端A","XJEC","DBU806",null,{"$f":"MID(D76,24,8)","v":"FC05A636"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["29","639042","error","IED(IF2201A)中存储的CCD校验码(FC05A636)与实际校验码(8303D9EC)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IF2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IF2201B","220kV母联智能终端B","XJEC","DBU806",null,{"$f":"MID(D81,24,8)","v":"A33C4E06"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["9","651354","error","IED(IF2201B)中存储的CCD校验码(A33C4E06)与实际校验码(AB132BC2)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1101A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1101A","1#主变低压侧智能终端A","XJEC","DBU816","智能终端",{"$f":"MID(D86,24,8)","v":"FEA78C53"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["33","237296","error","IED(IT1101A)中存储的CCD校验码(FEA78C53)与实际校验码(51B100AA)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1101B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1101B","1#主变低压侧智能终端B","XJEC","DBU816","智能终端",{"$f":"MID(D91,24,8)","v":"182DB222"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","245147","error","IED(IT1101B)中存储的CCD校验码(182DB222)与实际校验码(C802B34D)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1102A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1102A","2#主变中压侧智能终端A","XJEC","DBU816","智能终端",{"$f":"MID(D96,24,8)","v":"2ED368F0"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["33","307385","error","IED(IT1102A)中存储的CCD校验码(2ED368F0)与实际校验码(36026A43)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1102B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1102B","2#主变中压侧智能终端B","XJEC","DBU816","智能终端",{"$f":"MID(D101,24,8)","v":"F0ABFC7C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","315236","error","IED(IT1102B)中存储的CCD校验码(F0ABFC7C)与实际校验码(92D9AC45)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IM1101A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IM1101A","110kV I母线智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D106,24,8)","v":"FDDA7CB1"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["13","377332","error","IED(IM1101A)中存储的CCD校验码(FDDA7CB1)与实际校验码(666F0DCA)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IM1101B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IM1101B","110kVII母线智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D111,24,8)","v":"F87A9CD8"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["13","385173","error","IED(IM1101B)中存储的CCD校验码(F87A9CD8)与实际校验码(0F824A3D)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IML1107)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IML1107","110kV兴金线168智能组件","SIFANG","Template","合智一体",{"$f":"MID(D117,24,8)","v":"D67C5C3A"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["41","1130431","error","IED(IML1107)中访问点(M1:)下的LD(MUSV)SV控制块(MSVCB01)未配置网络参数","Q_CSG1204059-2020"]
["42","1124376","error","IED(IML1107)中存储的CCD校验码(D67C5C3A)与实际校验码(65857D19)不一致","GB/T 32890","5.3"]
["43","1124768","waring","IED(IML1107)中访问点(G1:)下的LD(RPIT)GOOSE控制块(GCB1)的appID(IML1107RPIT/LLN0$GO$GCB1)格式不符合规范","DL/T1873","10.2"]
["44","1124769","waring","IED(IML1107)中访问点(G1:)下的LD(RPIT)GOOSE控制块(GCB2)的appID(IML1107RPIT/LLN0$GO$GCB2)格式不符合规范","DL/T1873","10.2"]
["45","1124770","waring","IED(IML1107)中访问点(G1:)下的LD(RPIT)GOOSE控制块(GCB3)的appID(IML1107RPIT/LLN0$GO$GCB3)格式不符合规范","DL/T1873","10.2"]
["46","1124771","waring","IED(IML1107)中访问点(G1:)下的LD(RPIT)GOOSE控制块(GCB4)的appID(IML1107RPIT/LLN0$GO$GCB4)格式不符合规范","DL/T1873","10.2"]
["47","1130431","waring","IED(IML1107)中访问点(M1:)下的LD(MUSV)SV控制块(MSVCB01)的appID(IML1107MUSV/LLNO$SV$MSVCB01)格式不符合规范","DL/T1873","10.2"]
["  小金_160118.SCD-装置(IL1103)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1103","110kV固金线166智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D127,23,8)","v":"662E14D8"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["35","686364","error","IED(IL1103)中存储的CCD校验码(662E14D8)与实际校验码(4F66878E)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL1104)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1104","110kV备用线162智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D132,23,8)","v":"19D326A0"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["35","697718","error","IED(IL1104)中存储的CCD校验码(19D326A0)与实际校验码(A1BB3AAA)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL1106)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1106","110kV 备用线167智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D137,23,8)","v":"6264A046"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1104804","error","IED(IL1106)中存储的CCD校验码(6264A046)与实际校验码(EFBAB693)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1101","110kV备用线169智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D142,23,8)","v":"66E9F9B4"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["35","663656","error","IED(IL1101)中存储的CCD校验码(66E9F9B4)与实际校验码(FD709D51)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL1102)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1103","110kV固金线166智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D147,23,8)","v":"9870D4AE"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["35","675010","error","IED(IL1102)中存储的CCD校验码(9870D4AE)与实际校验码(9F7951E7)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IL1105)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IL1105","110kV金艺线165智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D152,23,8)","v":"70558192"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["35","1093450","error","IED(IL1105)中存储的CCD校验码(70558192)与实际校验码(6504B005)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IF1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IF1101","110kV母联智能终端","XJEC","DBU816","智能终端",{"$f":"MID(D157,23,8)","v":"B955CA6B"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["33","709072","error","IED(IF1101)中存储的CCD校验码(B955CA6B)与实际校验码(B5BEF40F)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ITB011)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ITB011","#1主变本体智能终端1",null,"DTU803","智能终端",{"$f":"MID(D162,23,8)","v":"BB5D530F"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["15","177050","error","IED(ITB011)中存储的CCD校验码(BB5D530F)与实际校验码(601DD858)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ITB012)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ITB012","#1主变本体智能终端2","XJEC","DTU803","智能终端",{"$f":"MID(D167,23,8)","v":"921520FB"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","180630","error","IED(ITB012)中存储的CCD校验码(921520FB)与实际校验码(4D750BCA)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ITB021)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ITB021","#2主变本体智能终端1","XJEC","DTU803","智能终端",{"$f":"MID(D172,23,8)","v":"2EFE4E48"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["15","191311","error","IED(ITB021)中存储的CCD校验码(2EFE4E48)与实际校验码(391B70F5)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ITB022)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ITB022","#2主变本体智能终端2","XJEC","DTU803","智能终端",{"$f":"MID(D177,23,8)","v":"F887A563"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","194891","error","IED(ITB022)中存储的CCD校验码(F887A563)与实际校验码(99FEF11E)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1001A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1001A","1#主变低压侧智能终端A","XJEC","DBU816","智能终端",{"$f":"MID(D182,24,8)","v":"4E2440C3"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["7","259987","error","IED(IT1001A)中存储的CCD校验码(4E2440C3)与实际校验码(4D4F8B13)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1001B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1001B","1#主变低压侧智能终端B","XJEC","DBU816","智能终端",{"$f":"MID(D187,24,8)","v":"874EACB3"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","267825","error","IED(IT1001B)中存储的CCD校验码(874EACB3)与实际校验码(E72246E6)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1002A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1002A","2#主变低压侧智能终端A","XJEC","DBU816","智能终端",{"$f":"MID(D192,24,8)","v":"FC997A1C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["7","330076","error","IED(IT1002A)中存储的CCD校验码(FC997A1C)与实际校验码(F0B32284)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(IT1002B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["IT1002B","2#主变低压侧智能终端B","XJEC","DBU816","智能终端",{"$f":"MID(D197,24,8)","v":"009D84A2"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["3","337914","error","IED(IT1002B)中存储的CCD校验码(009D84A2)与实际校验码(D6519053)不一致","GB/T 32890","5.3"]

{"sheet":"合并单元","index":3,"n_rows":202,"n_cols":6,"rows_kept":202,"cut":false,"hidden":false,"merged":[[0,0,0,5],[6,0,6,5],[12,0,12,5],[18,0,18,5],[24,0,24,5],[31,0,31,5],[38,0,38,5],[44,0,44,5],[50,0,50,5],[56,0,56,5],[62,0,62,5],[68,0,68,5],[74,0,74,5],[80,0,80,5],[86,0,86,5],[92,0,92,5],[98,0,98,5],[104,0,104,5],[110,0,110,5],[116,0,116,5],[122,0,122,5],[129,0,129,5],[136,0,136,5],[142,0,142,5],[148,0,148,5],[154,0,154,5],[160,0,160,5],[166,0,166,5],[172,0,172,5],[178,0,178,5],[184,0,184,5],[190,0,190,5],[196,0,196,5]]}
["  小金_160118.SCD-装置(MT2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT2201A","1#主变高压侧合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D6,24,8)","v":"1DBE31DC"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","205649","error","IED(MT2201A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","205572","error","IED(MT2201A)中存储的CCD校验码(1DBE31DC)与实际校验码(3374098A)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT2201B","1#主变高压侧合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D12,24,8)","v":"5ECD98A5"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","209204","error","IED(MT2201B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","209127","error","IED(MT2201B)中存储的CCD校验码(5ECD98A5)与实际校验码(5EFB91C1)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT2202A","2#主变高压侧合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D18,24,8)","v":"748EDB9F"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","275738","error","IED(MT2202A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","275661","error","IED(MT2202A)中存储的CCD校验码(748EDB9F)与实际校验码(055C11AF)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT2202B","2#主变高压侧合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D24,24,8)","v":"3C8C6B3C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","279293","error","IED(MT2202B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","279216","error","IED(MT2202B)中存储的CCD校验码(3C8C6B3C)与实际校验码(57C919FB)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MM2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MM2201A","220kV母线合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D31,24,8)","v":"EB47D0C9"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","345825","error","IED(MM2201A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","346537","error","IED(MM2201A)中访问点(M2:合并单元FT3)下的LD(MUSV02)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["3","345750","error","IED(MM2201A)中存储的CCD校验码(EB47D0C9)与实际校验码(44E5242E)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MM2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MM2201B","220kV母线合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D38,24,8)","v":"B7F53B96"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","349800","error","IED(MM2201B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","350512","error","IED(MM2201B)中访问点(M2:合并单元FT3)下的LD(MUSV02)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["3","349725","error","IED(MM2201B)中存储的CCD校验码(B7F53B96)与实际校验码(EDAA8F4F)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2201A","220kV丹金I线266合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D44,24,8)","v":"5241F791"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","586367","error","IED(ML2201A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","586292","error","IED(ML2201A)中存储的CCD校验码(5241F791)与实际校验码(D29EE21F)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2201B","220kV丹金I线266合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D50,24,8)","v":"9D21DF40"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","598685","error","IED(ML2201B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","598610","error","IED(ML2201B)中存储的CCD校验码(9D21DF40)与实际校验码(EB09E6A8)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2202A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2202A","220kV丹金II线265合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D56,24,8)","v":"B0041770"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","610991","error","IED(ML2202A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","610916","error","IED(ML2202A)中存储的CCD校验码(B0041770)与实际校验码(D2BC6B07)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2202B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2202B","220kV丹金II线265合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D62,24,8)","v":"80544075"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","623309","error","IED(ML2202B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","623234","error","IED(ML2202B)中存储的CCD校验码(80544075)与实际校验码(950A7A5D)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2203A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2203A","220kV木金线261合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D68,24,8)","v":"03964847"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1030489","error","IED(ML2203A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1030414","error","IED(ML2203A)中存储的CCD校验码(03964847)与实际校验码(2BD5A6E2)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2203B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2203B","220kV木金线261合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D74,24,8)","v":"8B381D99"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1037493","error","IED(ML2203B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1037418","error","IED(ML2203B)中存储的CCD校验码(8B381D99)与实际校验码(72184A1A)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2204A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2204A","220kV备用线264合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D80,24,8)","v":"F164707C"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1033991","error","IED(ML2204A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1033916","error","IED(ML2204A)中存储的CCD校验码(F164707C)与实际校验码(DE180567)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML2204B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML2204B","220kV备用线264合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D86,24,8)","v":"453F8753"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1040995","error","IED(ML2204B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1040920","error","IED(ML2204B)中存储的CCD校验码(453F8753)与实际校验码(F71BA9DB)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MF2201A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MF2201A","220kV母联合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D92,24,8)","v":"24470658"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","635615","error","IED(MF2201A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","635540","error","IED(MF2201A)中存储的CCD校验码(24470658)与实际校验码(115ED1DB)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MF2201B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MF2201B","220kV母联合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D98,24,8)","v":"D69A3EAE"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","647927","error","IED(MF2201B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","647852","error","IED(MF2201B)中存储的CCD校验码(D69A3EAE)与实际校验码(0F7C3123)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT1101A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT1101A","1#主变中压侧合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D104,24,8)","v":"7F977447"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","230367","error","IED(MT1101A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","230292","error","IED(MT1101A)中存储的CCD校验码(7F977447)与实际校验码(D0795169)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT1101B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT1101B","1#主变中压侧合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D110,24,8)","v":"58BAA394"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","233869","error","IED(MT1101B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","233794","error","IED(MT1101B)中存储的CCD校验码(58BAA394)与实际校验码(BD637998)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT1102A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT1102A","1#主变中压侧合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D116,24,8)","v":"CACC85A7"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","300456","error","IED(MT1102A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","300381","error","IED(MT1102A)中存储的CCD校验码(CACC85A7)与实际校验码(AEC92D5F)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MT1102B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MT1102B","1#主变中压侧合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D122,24,8)","v":"1F12711E"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","303958","error","IED(MT1102B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","303883","error","IED(MT1102B)中存储的CCD校验码(1F12711E)与实际校验码(84A620D2)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MM1101A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MM1101A","110kV母线合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D129,24,8)","v":"DE9076C5"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","369457","error","IED(MM1101A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","370169","error","IED(MM1101A)中访问点(M2:合并单元FT3)下的LD(MUSV02)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["3","369382","error","IED(MM1101A)中存储的CCD校验码(DE9076C5)与实际校验码(9D7D1772)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MM1101B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MM1101B","110kV母线合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D136,24,8)","v":"5FC9B399"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","373432","error","IED(MM1101B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","374144","error","IED(MM1101B)中访问点(M2:合并单元FT3)下的LD(MUSV02)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["3","373357","error","IED(MM1101B)中存储的CCD校验码(5FC9B399)与实际校验码(DFE96955)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1103)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1103","110kV固金线166合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D142,23,8)","v":"1810F93B"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","682937","error","IED(ML1103)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","682862","error","IED(ML1103)中存储的CCD校验码(1810F93B)与实际校验码(2F205857)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1104)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1104","110kV备用线162合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D148,23,8)","v":"13FFDE74"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","694291","error","IED(ML1104)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","694216","error","IED(ML1104)中存储的CCD校验码(13FFDE74)与实际校验码(AEADB44C)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1106)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1106","110kV备用线167合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D154,23,8)","v":"0EC2E9B0"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1101377","error","IED(ML1106)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1101302","error","IED(ML1106)中存储的CCD校验码(0EC2E9B0)与实际校验码(04DDA77B)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1101","110kV备用线169合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D160,23,8)","v":"8EC1ABF5"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","660229","error","IED(ML1101)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","660154","error","IED(ML1101)中存储的CCD校验码(8EC1ABF5)与实际校验码(A5783D00)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1102)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1102","110kV备用线170合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D166,23,8)","v":"0BDAAE38"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","671583","error","IED(ML1102)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","671508","error","IED(ML1102)中存储的CCD校验码(0BDAAE38)与实际校验码(1372C252)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(ML1105)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["ML1105","110kV金艺线165合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D172,23,8)","v":"34AFB021"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1090023","error","IED(ML1105)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","1089948","error","IED(ML1105)中存储的CCD校验码(34AFB021)与实际校验码(DA0FD025)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MF1101)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MF1101","110kV母联合并单元","XJEC","DMU-830","合并单元",{"$f":"MID(D178,23,8)","v":"E6652488"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","705645","error","IED(MF1101)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","705570","error","IED(MF1101)中存储的CCD校验码(E6652488)与实际校验码(62E7EC30)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MTB01A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MTB01A","#1主变本体合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D184,23,8)","v":"8332061E"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","184278","error","IED(MTB01A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","184201","error","IED(MTB01A)中存储的CCD校验码(8332061E)与实际校验码(0636C96A)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MTB01B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MTB01B","#1主变本体合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D190,23,8)","v":"FCDC29E5"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","187833","error","IED(MTB01B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","187756","error","IED(MTB01B)中存储的CCD校验码(FCDC29E5)与实际校验码(CFADB722)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MTB02A)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MTB02A","#2主变本体合并单元A","XJEC","DMU-830","合并单元",{"$f":"MID(D196,23,8)","v":"2095B9D0"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","198539","error","IED(MTB02A)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","198462","error","IED(MTB02A)中存储的CCD校验码(2095B9D0)与实际校验码(B2FFCC24)不一致","GB/T 32890","5.3"]
["  小金_160118.SCD-装置(MTB02B)校验结果"]
["装置编号","装置名称","厂家","型号","类型","校验码"]
["MTB02B","#1主变本体合并单元B","XJEC","DMU-830","合并单元",{"$f":"MID(D202,23,8)","v":"65DF5356"}]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","202094","error","IED(MTB02B)中访问点(M1:合并单元9-2)下的LD(MUSV01)SV控制块(smvcb0)未配置网络参数","Q_CSG1204059-2020"]
["2","202017","error","IED(MTB02B)中存储的CCD校验码(65DF5356)与实际校验码(FB6773F7)不一致","GB/T 32890","5.3"]

{"sheet":"schema语法和数据模板","index":4,"n_rows":515,"n_cols":6,"rows_kept":515,"cut":false,"hidden":false,"merged":[[0,0,0,5],[55,0,55,5],[65,0,65,5]]}
["  小金_160118.SCD-语法校验结果"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","2","waring","元素 SCL 中不允许出现属性 revision。"]
["2","2","waring","元素 SCL 中不允许出现属性 version。"]
["3","6699","waring","为元素 \"ConnectedAP\" 的身份约束条件声明的唯一值 [gocb8,RPIT] 重复。"]
["4","393013","waring","发现了以元素 IED 开头的无效内容。应以 {\"http://www.iec.ch/61850/2003/SCL\":IED, \"http://www.iec.ch/61850/2003/SCL\":DataTypeTemplates} 之一开头。"]
["5","458646","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["6","475004","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["7","493321","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["8","509679","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["9","551876","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["10","560427","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["11","738102","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["12","801137","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["13","801138","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["14","801139","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["15","801140","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["16","801141","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["17","801142","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["18","801143","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["19","801144","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["20","801199","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["21","801212","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["22","839528","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["23","867958","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["24","896393","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["25","924804","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["26","948770","waring","不是 integer 的有效值。"]
["27","948770","waring","在元素 ReportControl 中, 属性 intgPd 的值  与其类型 unsignedInt 不匹配。"]
["28","948772","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["29","948772","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["30","948777","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["31","948777","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["32","949700","waring","不是 integer 的有效值。"]
["33","949700","waring","在元素 ReportControl 中, 属性 intgPd 的值  与其类型 unsignedInt 不匹配。"]
["34","949702","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["35","949702","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["36","949707","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["37","949707","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["38","950099","waring","不是 integer 的有效值。"]
["39","950099","waring","在元素 ReportControl 中, 属性 intgPd 的值  与其类型 unsignedInt 不匹配。"]
["40","950101","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["41","950101","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["42","950106","waring","元素 OptFields 中不允许出现属性 bufOvfl。"]
["43","950106","waring","元素 OptFields 中不允许出现属性 segmentation。"]
["44","986982","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["45","998699","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["46","1014398","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["47","1029865","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["48","1130407","waring","元素 ExtRef 中必须包含属性 lnInst。"]
["49","1138789","waring","发现了以元素 LNodeType 开头的无效内容。应以 {\"http://www.iec.ch/61850/2003/SCL\":LNodeType, \"http://www.iec.ch/61850/2003/SCL\":DOType} 之一开头。"]
["50","1155299","waring","没有为元素 DataTypeTemplates 的身份约束条件找到值为 SZNR_CMV_SV 的关键字 ref2DOTypeForSDO。"]
["51","1155299","waring","没有为元素 DataTypeTemplates 的身份约束条件找到值为 SZNR_SPC_DC 的关键字 ref2DOType。"]
["52","1155300","waring","没有为元素 SCL 的身份约束条件找到值为 SZNR_LLN0_02,LLN0 的关键字 ref2LNodeTypeLLN0。"]
["53","1155300","waring","没有为元素 SCL 的身份约束条件找到值为 SZNR_LPHD,LPHD 的关键字 ref2LNodeTypeDomain2。"]
["  小金_160118.SCD-Communication校验结果"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","602779","error","IED(IL2201B)在GOOSE_B子网(GOOSE NETWORK B)下的控制块(gocb8)的appID(IL2201BRPIT/LLN0.gocb8)与IED(IL2201B)重复","QGDW11662-2017、Q/CSG1203065-2020","8.2.4"]
["2","1356","waring","IED(IT1001A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb1,ldInst=RPIT)的APPID(1143)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["3","1784","waring","IED(MM1101A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb1,ldInst=MUGO)的APPID(1155)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["4","1794","waring","IED(MM1101A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb2,ldInst=MUGO)的APPID(1156)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["5","1804","waring","IED(MM1101A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb3,ldInst=MUGO)的APPID(1157)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["6","1866","waring","IED(IM1101A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb3,ldInst=RPIT)的APPID(115A)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["7","2120","waring","IED(IL2201A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb2,ldInst=RPIT)的APPID(1168)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["8","2314","waring","IED(IL2202A)在GOOSE_A子网(GOOSE NETWORK A)下的控制块(cbName=gocb3,ldInst=RPIT)的APPID(1171)与mac地址不匹配","QGDW11662-2017","8.2.3"]
["  小金_160118.SCD-DataTypeTemplates校验结果"]
["序号","行号","等级","校验结果内容","应用标准","标准条款"]
["1","1153715","error","DOType(CN_DPC_NSV)中引用的DAType(Dbpos)不存在"]
["2","1155119","error","EnumType(setCharact)未被引用","DL/T1873","10.2"]
["3","1155229","error","EnumType(PolQty)未被引用","DL/T1873","10.2"]
["4","1155253","error","EnumType(RstMod)未被引用","DL/T1873","10.2"]
["5","1155098","error","EnumType(sev)未被引用","DL/T1873","10.2"]
["6","1155235","error","EnumType(POWCap)未被引用","DL/T1873","10.2"]
["7","1155223","error","EnumType(LevMod)未被引用","DL/T1873","10.2"]
["8","1155266","error","EnumType(SchTyp)未被引用","DL/T1873","10.2"]
["9","1155293","error","EnumType(WeiMod)未被引用","DL/T1873","10.2"]
["10","1155199","error","EnumType(DirMod)未被引用","DL/T1873","10.2"]
["11","1155110","error","EnumType(seqT)未被引用","DL/T1873","10.2"]
["12","1155114","error","EnumType(hvid)未被引用","DL/T1873","10.2"]
["13","1155216","error","EnumType(GnSt)未被引用","DL/T1873","10.2"]
["14","1155273","error","EnumType(TrgMod)未被引用","DL/T1873","10.2"]
["15","1155262","error","EnumType(RvAMod)未被引用","DL/T1873","10.2"]
["16","1155283","error","EnumType(TypRsCrv)未被引用","DL/T1873","10.2"]
["17","1155288","error","EnumType(UnBlkMod)未被引用","DL/T1873","10.2"]
["18","1155241","error","EnumType(OpMod)未被引用","DL/T1873","10.2"]
["19","1155278","error","EnumType(TrMod)未被引用","DL/T1873","10.2"]
["20","1155105","error","EnumType(phsid)未被引用","DL/T1873","10.2"]
["21","1155204","error","EnumType(FailMod)未被引用","DL/T1873","10.2"]
["22","1155210","error","EnumType(FanCtl)未被引用","DL/T1873","10.2"]
["23","1155245","error","EnumType(ReTrMod)未被引用","DL/T1873","10.2"]
["24","1154313","error","DAType(J_Originator)未被引用","DL/T1873","10.2"]
["25","1154181","error","DAType(CN_Originator)未被引用","DL/T1873","10.2"]
["26","1154333","error","DAType(J_Cancel_yk)未被引用","DL/T1873","10.2"]
["27","1154263","error","DAType(Originator)未被引用","DL/T1873","10.2"]
["28","1154317","error","DAType(J_SBOw_yk)未被引用","DL/T1873","10.2"]
["29","1131561","error","LNodeType(XJ_DevAlmGGIO_FCK851B_LD021)未被引用","DL/T1873","10.2"]
["30","1132862","error","LNodeType(XJ_LLN0_FCK851B_MEAS0)未被引用","DL/T1873","10.2"]
["31","1133152","error","LNodeType(GGIO1_DTU800)未被引用","DL/T1873","10.2"]
["32","1133196","error","LNodeType(GGIO2_DTU800)未被引用","DL/T1873","10.2"]
["33","1133214","error","LNodeType(GGIO3_DTU800)未被引用","DL/T1873","10.2"]
["34","1133300","error","LNodeType(GGIO4_DTU800)未被引用","DL/T1873","10.2"]
["35","1133331","error","LNodeType(LLN0_DTU800)未被引用","DL/T1873","10.2"]
["36","1133337","error","LNodeType(LPHD1_DTU800)未被引用","DL/T1873","10.2"]
["37","1133342","error","LNodeType(YLTC1_DTU800)未被引用","DL/T1873","10.2"]
["38","1133351","error","LNodeType(XSWI1_DTU800)未被引用","DL/T1873","10.2"]
["39","1133365","error","LNodeType(XJ_GGIO1_ALM_DMU800)未被引用","DL/T1873","10.2"]
["40","1133391","error","LNodeType(XJ_GGIO2_Ind_DMU800)未被引用","DL/T1873","10.2"]
["41","1133417","error","LNodeType(XJ_LLN0_DMU800)未被引用","DL/T1873","10.2"]
["42","1133423","error","LNodeType(XJ_LLN0_DMU800_EX)未被引用","DL/T1873","10.2"]
["43","1133430","error","LNodeType(XJ_TCTR_DMU800)未被引用","DL/T1873","10.2"]
["44","1133437","error","LNodeType(XJ_TVTR_DMU800)未被引用","DL/T1873","10.2"]
["45","1133444","error","LNodeType(XJ_TVTR_EX_DMU800)未被引用","DL/T1873","10.2"]
["46","1133480","error","LNodeType(XJ_GGIO3_GOIN_DMU800)未被引用","DL/T1873","10.2"]
["47","1133506","error","LNodeType(GGIO3_DBU800)未被引用","DL/T1873","10.2"]
["48","1133528","error","LNodeType(GGIO4_DBU800)未被引用","DL/T1873","10.2"]
["49","1133662","error","LNodeType(GGIO1_DBU800)未被引用","DL/T1873","10.2"]
["50","1133708","error","LNodeType(XCBR1_DBU800)未被引用","DL/T1873","10.2"]
["51","1133721","error","LNodeType(XCBR1_DBU8000_EX)未被引用","DL/T1873","10.2"]
["52","1133737","error","LNodeType(GGIO5_DBU800)未被引用","DL/T1873","10.2"]
["53","1133787","error","LNodeType(GGIO6_DBU800)未被引用","DL/T1873","10.2"]
["54","1133809","error","LNodeType(GGIO7_DBU800)未被引用","DL/T1873","10.2"]
["55","1133826","error","LNodeType(GGIO3_DBU8000)未被引用","DL/T1873","10.2"]
["56","1133848","error","LNodeType(GGIO4_DBU8000)未被引用","DL/T1873","10.2"]
["57","1133982","error","LNodeType(IHMI)未被引用","DL/T1873","10.2"]
["58","1133988","error","LNodeType(GGIO3_DBU80000)未被引用","DL/T1873","10.2"]
["59","1134345","error","LNodeType(XJ_GGIO_WBH801B_PROT10)未被引用","DL/T1873","10.2"]
["60","1134769","error","LNodeType(NRR_LLN0_90X)未被引用","DL/T1873","10.2"]
["61","1134793","error","LNodeType(NRR_LPHD_931)未被引用","DL/T1873","10.2"]
["62","1134812","error","LNodeType(NRR_GGIO_SPC)未被引用","DL/T1873","10.2"]
["63","1134826","error","LNodeType(NRR_GGIO_IND)未被引用","DL/T1873","10.2"]
["64","1134840","error","LNodeType(NRR_GGIO_ALM)未被引用","DL/T1873","10.2"]
["65","1134854","error","LNodeType(NRR_PDIF_LINE)未被引用","DL/T1873","10.2"]
["66","1134877","error","LNodeType(NRR_PDIS_LINE)未被引用","DL/T1873","10.2"]
["67","1134899","error","LNodeType(NRR_PDIS)未被引用","DL/T1873","10.2"]
["68","1134916","error","LNodeType(NRR_PTOC)未被引用","DL/T1873","10.2"]
["69","1134940","error","LNodeType(NRR_PPDP)未被引用","DL/T1873","10.2"]
["70","1134952","error","LNodeType(NRR_PSCH)未被引用","DL/T1873","10.2"]
["71","1134974","error","LNodeType(NRR_RPSB)未被引用","DL/T1873","10.2"]
["72","1134986","error","LNodeType(NRR_PTRC)未被引用","DL/T1873","10.2"]
["73","1135005","error","LNodeType(NRR_RREC)未被引用","DL/T1873","10.2"]
["74","1135034","error","LNodeType(NRR_RFLO)未被引用","DL/T1873","10.2"]
["75","1135051","error","LNodeType(NRR_TVTR)未被引用","DL/T1873","10.2"]
["76","1135068","error","LNodeType(NRR_TCTR)未被引用","DL/T1873","10.2"]
["77","1135088","error","LNodeType(NRR_MMXU)未被引用","DL/T1873","10.2"]
["78","1135098","error","LNodeType(NRR_GGIO_ACT)未被引用","DL/T1873","10.2"]
["79","1135112","error","LNodeType(NRR_CILO)未被引用","DL/T1873","10.2"]
["80","1135121","error","LNodeType(NRR_RSYN)未被引用","DL/T1873","10.2"]
["81","1135163","error","LNodeType(NRR_CSWI)未被引用","DL/T1873","10.2"]
["82","1135176","error","LNodeType(NRR_GGIO_INT8U)未被引用","DL/T1873","10.2"]
["83","1135190","error","LNodeType(NRR_GGIO_DPC)未被引用","DL/T1873","10.2"]
["84","1135204","error","LNodeType(NRR_MMXU_Mea)未被引用","DL/T1873","10.2"]
["85","1135220","error","LNodeType(NRR_MMXU_Har)未被引用","DL/T1873","10.2"]
["86","1135242","error","LNodeType(NRR_GGIO_AnIn)未被引用","DL/T1873","10.2"]
["87","1135256","error","LNodeType(NRR_RDRE)未被引用","DL/T1873","10.2"]
["88","1135269","error","LNodeType(NRR_GGIO_SAV)未被引用","DL/T1873","10.2"]
["89","1135862","error","LNodeType(XJ_GGIO9_BDH800)未被引用","DL/T1873","10.2"]
["90","1135883","error","LNodeType(XJ_GGIO1_BDH800)未被引用","DL/T1873","10.2"]
["91","1135901","error","LNodeType(XJ_GGIO2_BDH800)未被引用","DL/T1873","10.2"]
["92","1135936","error","LNodeType(XJ_GGIO3_BDH800)未被引用","DL/T1873","10.2"]
["93","1135944","error","LNodeType(XJ_LLN0_BDH800_EX)未被引用","DL/T1873","10.2"]
["94","1135951","error","LNodeType(XJ_TVTR1_BDH800)未被引用","DL/T1873","10.2"]
["95","1135958","error","LNodeType(XJ_LLN0_BDH800)未被引用","DL/T1873","10.2"]
["96","1135964","error","LNodeType(XJ_TVTR1_BDH800_EX)未被引用","DL/T1873","10.2"]
["97","1136003","error","LNodeType(CSC103BE/LD0/LLN0)未被引用","DL/T1873","10.2"]
["98","1136026","error","LNodeType(CSC103BE/PROT/LLN0)未被引用","DL/T1873","10.2"]
["99","1136105","error","LNodeType(CSC103BE/SVLD/TVTR)未被引用","DL/T1873","10.2"]
["100","1136119","error","LNodeType(CSC103BE/PI/GGIO6)未被引用","DL/T1873","10.2"]
["101","1136195","error","LNodeType(CSC103BE/PI/RBRF1)未被引用","DL/T1873","10.2"]
["102","1136210","error","LNodeType(CSC103BE/PROT/PTOC7)未被引用","DL/T1873","10.2"]
["103","1136219","error","LNodeType(CSC103BE/PROT/PTOC6)未被引用","DL/T1873","10.2"]
["104","1136229","error","LNodeType(CSC103BE/PROT/PDIS7)未被引用","DL/T1873","10.2"]
["105","1136239","error","LNodeType(CSC103BE/PROT/PDIS6)未被引用","DL/T1873","10.2"]
["106","1136249","error","LNodeType(CSC103BE/PROT/PDIS5)未被引用","DL/T1873","10.2"]
["107","1136258","error","LNodeType(CSC103BE/PROT/PDIS4)未被引用","DL/T1873","10.2"]
["108","1136268","error","LNodeType(CSC103BE/PROT/PDIS3)未被引用","DL/T1873","10.2"]
["109","1136278","error","LNodeType(CSC103BE/PROT/PDIS2)未被引用","DL/T1873","10.2"]
["110","1136291","error","LNodeType(CSC103BE/PROT/RREC2)未被引用","DL/T1873","10.2"]
["111","1136302","error","LNodeType(CSC103BE/PROT/RBRF2)未被引用","DL/T1873","10.2"]
["112","1136312","error","LNodeType(CSC103BE/PROT/RBRF1)未被引用","DL/T1873","10.2"]
["113","1136320","error","LNodeType(CSC103BE/PROT/PTOC5)未被引用","DL/T1873","10.2"]
["114","1136329","error","LNodeType(CSC103BE/PROT/PTOC4)未被引用","DL/T1873","10.2"]
["115","1136340","error","LNodeType(CSC103BE/PROT/PDIF9)未被引用","DL/T1873","10.2"]
["116","1136349","error","LNodeType(CSC103BE/PROT/PDIF8)未被引用","DL/T1873","10.2"]
["117","1136362","error","LNodeType(CSC103BE/PROT/RREC1)未被引用","DL/T1873","10.2"]
["118","1136370","error","LNodeType(CSC103BE/PROT/PTOC3)未被引用","DL/T1873","10.2"]
["119","1136378","error","LNodeType(CSC103BE/PROT/PTOC2)未被引用","DL/T1873","10.2"]
["120","1136388","error","LNodeType(CSC103BE/PROT/PTOC1)未被引用","DL/T1873","10.2"]
["121","1136398","error","LNodeType(CSC103BE/PROT/PDIF7)未被引用","DL/T1873","10.2"]
["122","1136408","error","LNodeType(CSC103BE/PROT/PDIF6)未被引用","DL/T1873","10.2"]
["123","1136421","error","LNodeType(CSC103BE/PROT/PDIS1)未被引用","DL/T1873","10.2"]
["124","1136437","error","LNodeType(CSC103BE/PROT/PDIF4)未被引用","DL/T1873","10.2"]
["125","1136446","error","LNodeType(CSC103BE/PROT/PDIF3)未被引用","DL/T1873","10.2"]
["126","1136455","error","LNodeType(CSC103BE/PROT/PDIF2)未被引用","DL/T1873","10.2"]
["127","1136464","error","LNodeType(CSC103BE/PROT/PDIF1)未被引用","DL/T1873","10.2"]
["128","1136473","error","LNodeType(CSC103BE/PROT/RFLO1)未被引用","DL/T1873","10.2"]
["129","1136499","error","LNodeType(CSC103BE/MEAS/MMXU6)未被引用","DL/T1873","10.2"]
["130","1136506","error","LNodeType(CSC103BE/MEAS/MMXU5)未被引用","DL/T1873","10.2"]
["131","1136528","error","LNodeType(CSC103BE/MEAS/MMXU2)未被引用","DL/T1873","10.2"]
["132","1136535","error","LNodeType(CSC103BE/MEAS/MMXU1)未被引用","DL/T1873","10.2"]
["133","1136751","error","LNodeType(CSC103BE/LD0/GGIO2)未被引用","DL/T1873","10.2"]
["134","1136827","error","LNodeType(CSC103BE/LD0/GGIO1)未被引用","DL/T1873","10.2"]
["135","1136854","error","LNodeType(CSC103BE/LD0/LLN00)未被引用","DL/T1873","10.2"]
["136","1137005","error","LNodeType(XJ_TCTR1_BDH800)未被引用","DL/T1873","10.2"]
["137","1137506","error","LNodeType(XJ_GOINGGIO_WMH800B_PI025)未被引用","DL/T1873","10.2"]
["138","1137519","error","LNodeType(XJ_GOINGGIO_WMH800B_PI024)未被引用","DL/T1873","10.2"]
["139","1137532","error","LNodeType(XJ_GOINGGIO_WMH800B_PI023)未被引用","DL/T1873","10.2"]
["140","1137545","error","LNodeType(XJ_GOINGGIO_WMH800B_PI022)未被引用","DL/T1873","10.2"]
["141","1137558","error","LNodeType(XJ_GOINGGIO_WMH800B_PI021)未被引用","DL/T1873","10.2"]
["142","1137571","error","LNodeType(XJ_GOINGGIO_WMH800B_PI020)未被引用","DL/T1873","10.2"]
["143","1137584","error","LNodeType(XJ_GOINGGIO_WMH800B_PI019)未被引用","DL/T1873","10.2"]
["144","1137597","error","LNodeType(XJ_GOINGGIO_WMH800B_PI018)未被引用","DL/T1873","10.2"]
["145","1137610","error","LNodeType(XJ_GOINGGIO_WMH800B_PI017)未被引用","DL/T1873","10.2"]
["146","1137623","error","LNodeType(XJ_GOINGGIO_WMH800B_PI016)未被引用","DL/T1873","10.2"]
["147","1137636","error","LNodeType(XJ_GOINGGIO_WMH800B_PI015)未被引用","DL/T1873","10.2"]
["148","1137649","error","LNodeType(XJ_GOINGGIO_WMH800B_PI014)未被引用","DL/T1873","10.2"]
["149","1137662","error","LNodeType(XJ_GOINGGIO_WMH800B_PI013)未被引用","DL/T1873","10.2"]
["150","1137675","error","LNodeType(XJ_GOINGGIO_WMH800B_PI012)未被引用","DL/T1873","10.2"]
["151","1137688","error","LNodeType(XJ_GOINGGIO_WMH800B_PI011)未被引用","DL/T1873","10.2"]
["152","1137701","error","LNodeType(XJ_GOINGGIO_WMH800B_PI010)未被引用","DL/T1873","10.2"]
["153","1137714","error","LNodeType(XJ_GOINGGIO_WMH800B_PI09)未被引用","DL/T1873","10.2"]
["154","1137727","error","LNodeType(XJ_GOINGGIO_WMH800B_PI08)未被引用","DL/T1873","10.2"]
["155","1137740","error","LNodeType(XJ_GOINGGIO_WMH800B_PI07)未被引用","DL/T1873","10.2"]
["156","1137753","error","LNodeType(XJ_GOINGGIO_WMH800B_PI06)未被引用","DL/T1873","10.2"]
["157","1137766","error","LNodeType(XJ_GOINGGIO_WMH800B_PI05)未被引用","DL/T1873","10.2"]
["158","1137779","error","LNodeType(XJ_GOINGGIO_WMH800B_PI04)未被引用","DL/T1873","10.2"]
["159","1137792","error","LNodeType(XJ_GOINGGIO_WMH800B_PI03)未被引用","DL/T1873","10.2"]
["160","1137805","error","LNodeType(XJ_GOINGGIO_WMH800B_PI02)未被引用","DL/T1873","10.2"]
["161","1137818","error","LNodeType(XJ_GOINGGIO_WMH800B_PI01)未被引用","DL/T1873","10.2"]
["162","1137842","error","LNodeType(XJ_PTRC_WMH800B_PI01)未被引用","DL/T1873","10.2"]
["163","1138544","error","LNodeType(XJ_RBRF_WMH800B_PROT2)未被引用","DL/T1873","10.2"]
["164","1138789","error","LNodeType(SZNR_LLN0_0)未被引用","DL/T1873","10.2"]
["165","1138796","error","LNodeType(SZNR_LLN0_1_PRS7K)未被引用","DL/T1873","10.2"]
["166","1139130","error","LNodeType(SZNR_MMXU_RLY_PRS7K)未被引用","DL/T1873","10.2"]
["167","1139265","error","LNodeType(SZNR_YPTR_PRS7K)未被引用","DL/T1873","10.2"]
["168","1139278","error","LNodeType(SZNR_PDIF_PRS7K)未被引用","DL/T1873","10.2"]
["169","1139297","error","LNodeType(SZNR_PDIS_PRS7K)未被引用","DL/T1873","10.2"]
["170","1139317","error","LNodeType(SZNR_PVOC_PRS7K)未被引用","DL/T1873","10.2"]
["171","1139334","error","LNodeType(SZNR_PTOV_PRS7K)未被引用","DL/T1873","10.2"]
["172","1139348","error","LNodeType(SZNR_RBRF_PRS7K)未被引用","DL/T1873","10.2"]
["173","1139367","error","LNodeType(SZNR_PTOC_PRS7K)未被引用","DL/T1873","10.2"]
["174","1139551","error","LNodeType(SZNR_TVTR_PRS7K)未被引用","DL/T1873","10.2"]
["175","1139564","error","LNodeType(SZNR_TCTR_PRS7K)未被引用","DL/T1873","10.2"]
["176","1139576","error","LNodeType(CSC122ME/LD0/LLN0)未被引用","DL/T1873","10.2"]
["177","1139620","error","LNodeType(CSC122ME/PROT/LLN0)未被引用","DL/T1873","10.2"]
["178","1139670","error","LNodeType(CSC122ME/PI/GGIO4)未被引用","DL/T1873","10.2"]
["179","1139677","error","LNodeType(CSC122ME/PI/GGIO1)未被引用","DL/T1873","10.2"]
["180","1139715","error","LNodeType(CSC122ME/MEAS/SIML1)未被引用","DL/T1873","10.2"]
["181","1139723","error","LNodeType(CSC122ME/MEAS/ZBAT1)未被引用","DL/T1873","10.2"]
["182","1139730","error","LNodeType(CSC122ME/MEAS/MMXN6)未被引用","DL/T1873","10.2"]
["183","1139737","error","LNodeType(CSC122ME/MEAS/MMXN5)未被引用","DL/T1873","10.2"]
["184","1139744","error","LNodeType(CSC122ME/MEAS/MMXN4)未被引用","DL/T1873","10.2"]
["185","1139751","error","LNodeType(CSC122ME/MEAS/MMXN3)未被引用","DL/T1873","10.2"]
["186","1139758","error","LNodeType(CSC122ME/MEAS/MMXN2)未被引用","DL/T1873","10.2"]
["187","1139765","error","LNodeType(CSC122ME/MEAS/MMXN1)未被引用","DL/T1873","10.2"]
["188","1139772","error","LNodeType(CSC122ME/MEAS/MMXU5)未被引用","DL/T1873","10.2"]
["189","1139780","error","LNodeType(CSC122ME/MEAS/MMXU4)未被引用","DL/T1873","10.2"]
["190","1139787","error","LNodeType(CSC122ME/MEAS/MMXU3)未被引用","DL/T1873","10.2"]
["191","1139795","error","LNodeType(CSC122ME/MEAS/MMXU2)未被引用","DL/T1873","10.2"]
["192","1139802","error","LNodeType(CSC122ME/MEAS/MMXU1)未被引用","DL/T1873","10.2"]
["193","1139810","error","LNodeType(CSC122ME/LD0/GGIO3)未被引用","DL/T1873","10.2"]
["194","1139836","error","LNodeType(CSC122ME/LD0/GGIO2)未被引用","DL/T1873","10.2"]
["195","1139934","error","LNodeType(CSC122ME/LD0/GGIO1)未被引用","DL/T1873","10.2"]
["196","1139944","error","LNodeType(CSC122ME/CTRL/RSYN1)未被引用","DL/T1873","10.2"]
["197","1139961","error","LNodeType(CSC122ME/CTRL/RSYN2)未被引用","DL/T1873","10.2"]
["198","1139975","error","LNodeType(CSC122ME/CTRL/RSYN3)未被引用","DL/T1873","10.2"]
["199","1139983","error","LNodeType(CSC122ME/CTRL/XCBR1)未被引用","DL/T1873","10.2"]
["200","1139995","error","LNodeType(CSC122ME/CTRL/CILO1)未被引用","DL/T1873","10.2"]
["201","1140003","error","LNodeType(CSC122ME/CTRL/XSWI1)未被引用","DL/T1873","10.2"]
["202","1140016","error","LNodeType(CSC122ME/CTRL/CSWI1)未被引用","DL/T1873","10.2"]
["203","1140024","error","LNodeType(CSC122ME/CTRL/GGIO1DO)未被引用","DL/T1873","10.2"]
["204","1140031","error","LNodeType(CSC122ME/CTRL/GGIO2)未被引用","DL/T1873","10.2"]
["205","1140087","error","LNodeType(SZNR_LLN0_00)未被引用","DL/T1873","10.2"]
["206","1140094","error","LNodeType(SZNR_LLN0_GOOSE_PRS7K0)未被引用","DL/T1873","10.2"]
["207","1140101","error","LNodeType(SZNR_LLN0_1_BP2C)未被引用","DL/T1873","10.2"]
["208","1140333","error","LNodeType(SZNR_LPHD0)未被引用","DL/T1873","10.2"]
["209","1140338","error","LNodeType(SZNR_GGIO_CHK_BP2C)未被引用","DL/T1873","10.2"]
["210","1140403","error","LNodeType(SZNR_GGIO_GOALM_BP2C)未被引用","DL/T1873","10.2"]
["211","1140697","error","LNodeType(SZNR_GGIO_SVALM_BP2C)未被引用","DL/T1873","10.2"]
["212","1140847","error","LNodeType(SZNR_MMXU_RLY_BP2C)未被引用","DL/T1873","10.2"]
["213","1140857","error","LNodeType(SZNR_GGIO_ALM_BP2C)未被引用","DL/T1873","10.2"]
["214","1140903","error","LNodeType(SZNR_GGIO_RlyDin_BP2C)未被引用","DL/T1873","10.2"]
["215","1140953","error","LNodeType(SZNR_RDRE_PRS7K0)未被引用","DL/T1873","10.2"]
["216","1140962","error","LNodeType(SZNR_PDIF_BUS_BP2C)未被引用","DL/T1873","10.2"]
["217","1140975","error","LNodeType(SZNR_RBRF_BUS_BP2C)未被引用","DL/T1873","10.2"]
["218","1140992","error","LNodeType(SZNR_RBRF_BUSC_BP2C)未被引用","DL/T1873","10.2"]
["219","1141002","error","LNodeType(SZNR_PTOC_PGE_BP2C)未被引用","DL/T1873","10.2"]
["220","1141013","error","LNodeType(SZNR_PTOC_PGEI0_BP2C)未被引用","DL/T1873","10.2"]
["221","1141023","error","LNodeType(SZNR_TVTR_BUS_BP2C)未被引用","DL/T1873","10.2"]
["222","1141036","error","LNodeType(SZNR_TCTR_BAY_BP2C)未被引用","DL/T1873","10.2"]
["223","1141048","error","LNodeType(SZNR_GGIO_ACT_BP2C)未被引用","DL/T1873","10.2"]
["224","1141105","error","LNodeType(SZNR_PTRC_GOOUT_BP2C)未被引用","DL/T1873","10.2"]
["225","1141114","error","LNodeType(SZNR_GGIO_SIG48_BP2C)未被引用","DL/T1873","10.2"]
["226","1141168","error","LNodeType(SZNR_GGIO_GOBIN_BP2C)未被引用","DL/T1873","10.2"]
["227","1141180","error","LNodeType(SZNR_GGIO_GOIN_BP2C)未被引用","DL/T1873","10.2"]
["228","1141238","error","LNodeType(XJ_ZYPTOC_WBH801B_PROT100)未被引用","DL/T1873","10.2"]
["229","1141249","error","LNodeType(XJ_DY2PTOC_WBH801B_PROT21)未被引用","DL/T1873","10.2"]
["230","1141258","error","LNodeType(XJ_ZYPTOC_WBH801B_PROT120)未被引用","DL/T1873","10.2"]
["231","1141268","error","LNodeType(XJ_ZYPDIS_WBH801B_PROT3)未被引用","DL/T1873","10.2"]
["232","1141279","error","LNodeType(XJ_ZYPDIS_WBH801B_PROT80)未被引用","DL/T1873","10.2"]
["233","1141288","error","LNodeType(XJ_ZYPDIS_WBH801B_PROT70)未被引用","DL/T1873","10.2"]
["234","1141300","error","LNodeType(XJ_GRPTOC_WBH801B_PROT22)未被引用","DL/T1873","10.2"]
["235","1141310","error","LNodeType(XJ_GYPTRC_WBH801B_PI01)未被引用","DL/T1873","10.2"]
["236","1141317","error","LNodeType(XJ_GYPTRC_WBH801B_PI030)未被引用","DL/T1873","10.2"]
["237","1141324","error","LNodeType(XJ_GYPTRC_WBH801B_PI040)未被引用","DL/T1873","10.2"]
["238","1141331","error","LNodeType(XJ_ZYPTRC_WBH801B_PI05)未被引用","DL/T1873","10.2"]
["239","1141338","error","LNodeType(XJ_ZYPTRC_WBH801B_PI06)未被引用","DL/T1873","10.2"]
["240","1141345","error","LNodeType(XJ_ZYPTRC_WBH801B_PI080)未被引用","DL/T1873","10.2"]
["241","1141352","error","LNodeType(XJ_DY1PTRC_WBH801B_PI09)未被引用","DL/T1873","10.2"]
["242","1141359","error","LNodeType(XJ_DY1PTRC_WBH801B_PI010)未被引用","DL/T1873","10.2"]
["243","1141366","error","LNodeType(XJ_DY2PTRC_WBH801B_PI011)未被引用","DL/T1873","10.2"]
["244","1141373","error","LNodeType(XJ_DY2PTRC_WBH801B_PI012)未被引用","DL/T1873","10.2"]
["245","1141380","error","LNodeType(XJ_ZYPTRC_WBH801B_PI0130)未被引用","DL/T1873","10.2"]
["246","1141387","error","LNodeType(XJ_DY1PTRC_WBH801B_PI014)未被引用","DL/T1873","10.2"]
["247","1141394","error","LNodeType(XJ_DY2PTRC_WBH801B_PI015)未被引用","DL/T1873","10.2"]
["248","1141401","error","LNodeType(XJ_GYPTRC_WBH801B_PI0160)未被引用","DL/T1873","10.2"]
["249","1141408","error","LNodeType(XJ_PTRC_WBH801B_PI0170)未被引用","DL/T1873","10.2"]
["250","1141415","error","LNodeType(XJ_PTRC_WBH801B_PI0180)未被引用","DL/T1873","10.2"]
["251","1141422","error","LNodeType(XJ_PTRC_WBH801B_PI0190)未被引用","DL/T1873","10.2"]
["252","1141429","error","LNodeType(XJ_PTRC_WBH801B_PI0200)未被引用","DL/T1873","10.2"]
["253","1141436","error","LNodeType(XJ_GOINGGIO_WBH801B_PI02)未被引用","DL/T1873","10.2"]
["254","1141446","error","LNodeType(CSC103BE/LD0/LLN01)未被引用","DL/T1873","10.2"]
["255","1141469","error","LNodeType(CSC103BE/PROT/LLN00)未被引用","DL/T1873","10.2"]
["256","1141570","error","LNodeType(CSC103BE/MEAS/MMXN2)未被引用","DL/T1873","10.2"]
["257","1141577","error","LNodeType(CSC103BE/MEAS/MMXN1)未被引用","DL/T1873","10.2"]
["258","1141584","error","LNodeType(CSC103BE/MEAS/MMXU20)未被引用","DL/T1873","10.2"]
["259","1141591","error","LNodeType(CSC103BE/MEAS/MMXU10)未被引用","DL/T1873","10.2"]
["260","1141598","error","LNodeType(CSC103BE/LD0/GGIO20)未被引用","DL/T1873","10.2"]
["261","1141681","error","LNodeType(CSC122ME/CTRL/XCBR10)未被引用","DL/T1873","10.2"]
["262","1141693","error","LNodeType(CSC122ME/CTRL/XSWI10)未被引用","DL/T1873","10.2"]
["263","1141706","error","LNodeType(NRR_PDIF_BUS)未被引用","DL/T1873","10.2"]
["264","1141731","error","LNodeType(XJ_DevGOINGGIO_FCK851B_PI062)未被引用","DL/T1873","10.2"]
["265","1141757","error","LNodeType(XJ_DevGOINGGIO_FCK851B_CTRL5)未被引用","DL/T1873","10.2"]
["266","1141773","error","LNodeType(XJ_LgcINGGIO_FCK851B_CTRL41)未被引用","DL/T1873","10.2"]
["267","1141786","error","LNodeType(XJ_LinMMXU_FCK851B_MEAS1)未被引用","DL/T1873","10.2"]
["268","1141806","error","LNodeType(XJ_TVTR_FCK851B_MEAS1)未被引用","DL/T1873","10.2"]
["269","1141814","error","LNodeType(XJ_TCTR_FCK851B_MEAS1)未被引用","DL/T1873","10.2"]
["270","1141823","error","LNodeType(XJ_GOGGIO_FCK851B_PROT11)未被引用","DL/T1873","10.2"]
["271","1141837","error","LNodeType(XJ_DevGOIN4GGIO_FCK851B_PI018)未被引用","DL/T1873","10.2"]
["272","1141851","error","LNodeType(XJ_LgcINGGIO_FCK851B_CTRL130)未被引用","DL/T1873","10.2"]
["273","1141889","error","LNodeType(XJ_Bus4MMXU_FCK851B_MEAS4)未被引用","DL/T1873","10.2"]
["274","1141898","error","LNodeType(XJ_TVTR_FCK851B_MEAS12)未被引用","DL/T1873","10.2"]
["275","1141917","error","LNodeType(XJ_GO4GGIO_FCK851B_PROT4)未被引用","DL/T1873","10.2"]
["276","1141988","error","LNodeType(XJ_LgcGOINGGIO_FCK852B_CTRL2)未被引用","DL/T1873","10.2"]
["277","1142000","error","LNodeType(XJ_GenGOINGGIO_FCK852B_CTRL1)未被引用","DL/T1873","10.2"]
["278","1142054","error","LNodeType(XJ_ATCC_FCK852B_CTRL1)未被引用","DL/T1873","10.2"]
["279","1142062","error","LNodeType(XJ_TVTR_FCK852B_MEAS1)未被引用","DL/T1873","10.2"]
["280","1142071","error","LNodeType(XJ_TCTR_FCK852B_MEAS1)未被引用","DL/T1873","10.2"]
["281","1142096","error","LNodeType(XJ_LLN0_FCK852B_PROT)未被引用","DL/T1873","10.2"]
["282","1142202","error","LNodeType(XJ_ATCC_FCK852B_CTRL10)未被引用","DL/T1873","10.2"]
["283","1142213","error","LNodeType(XJ_Lin2MMXU_FCK852B_MEAS2)未被引用","DL/T1873","10.2"]
["284","1142263","error","LNodeType(XJ_DevAlmGGIO_FCK852B_LD020)未被引用","DL/T1873","10.2"]
["285","1142991","error","LNodeType(XJ_DevAlmGGIO_FCK851B_LD023)未被引用","DL/T1873","10.2"]
["286","1144433","error","LNodeType(XJ_GGIO2_BDH8000)未被引用","DL/T1873","10.2"]
["287","1144457","error","LNodeType(GGIO2_DTU8000)未被引用","DL/T1873","10.2"]
["288","1144475","error","LNodeType(XSWI1_DTU8000)未被引用","DL/T1873","10.2"]
["289","1144832","error","LNodeType(XJ_AccGOINGGIO_FCK851B_PI05)未被引用","DL/T1873","10.2"]
["290","1144838","error","LNodeType(XJ_LLN0_FCK851B_LD03)未被引用","DL/T1873","10.2"]
["291","1144847","error","LNodeType(XJ_DevGOINGGIO_FCK851B_PI063)未被引用","DL/T1873","10.2"]
["292","1144883","error","LNodeType(XJ_DevGOINGGIO_FCK851B_CTRL50)未被引用","DL/T1873","10.2"]
["293","1144904","error","LNodeType(XJ_MMTR_FCK851B_MEAS1)未被引用","DL/T1873","10.2"]
["294","1146317","error","LNodeType(SZNR_PTOC_PGE_BP2C0)未被引用","DL/T1873","10.2"]
["295","1146328","error","LNodeType(SZNR_PTOC_PGEI0_BP2C0)未被引用","DL/T1873","10.2"]
["296","1146657","error","LNodeType(SZNR_LLN0_1_PRS713D)未被引用","DL/T1873","10.2"]
["297","1146733","error","LNodeType(SZNR_GGIO_CHK_PRS713D)未被引用","DL/T1873","10.2"]
["298","1146796","error","LNodeType(SZNR_GGIO_SYX_PRS713D)未被引用","DL/T1873","10.2"]
["299","1146882","error","LNodeType(SZNR_GGIO_TYX_PRS713D)未被引用","DL/T1873","10.2"]
["300","1146904","error","LNodeType(SZNR_MMXU_YC_PRS713D)未被引用","DL/T1873","10.2"]
["301","1146933","error","LNodeType(SZNR_RFLO_PRS7K)未被引用","DL/T1873","10.2"]
["302","1146941","error","LNodeType(SZNR_GGIO_GOALM_PRS713D)未被引用","DL/T1873","10.2"]
["303","1146995","error","LNodeType(SZNR_GGIO_BAYGSE_PRS713D)未被引用","DL/T1873","10.2"]
["304","1147033","error","LNodeType(SZNR_GGIO_SVALM_PRS713D)未被引用","DL/T1873","10.2"]
["305","1147183","error","LNodeType(SZNR_MMXU_RLY_PRS713D)未被引用","DL/T1873","10.2"]
["306","1147193","error","LNodeType(SZNR_GGIO_GOout48_PRS713D)未被引用","DL/T1873","10.2"]
["307","1147247","error","LNodeType(SZNR_GGIO_ALM_PRS713D)未被引用","DL/T1873","10.2"]
["308","1147318","error","LNodeType(SZNR_TVTR_PRS713D)未被引用","DL/T1873","10.2"]
["309","1147331","error","LNodeType(SZNR_PSCH_TD_PRS713D)未被引用","DL/T1873","10.2"]
["310","1147352","error","LNodeType(SZNR_RRTC_PRS713D)未被引用","DL/T1873","10.2"]
["311","1147374","error","LNodeType(SZNR_PDIF_CD_PRS713D)未被引用","DL/T1873","10.2"]
["312","1147400","error","LNodeType(SZNR_PTRC_TZ_PRS713D)未被引用","DL/T1873","10.2"]
["313","1147417","error","LNodeType(SZNR_PPDP_BYZ_PRS713D)未被引用","DL/T1873","10.2"]
["314","1147431","error","LNodeType(SZNR_PDIS_JL_PRS713D)未被引用","DL/T1873","10.2"]
["315","1147461","error","LNodeType(SZNR_PTOC_PRS713D)未被引用","DL/T1873","10.2"]
["316","1147478","error","LNodeType(SZNR_PTOV_PRS713D)未被引用","DL/T1873","10.2"]
["317","1147491","error","LNodeType(SZNR_RPSB_ZD_PRS713D)未被引用","DL/T1873","10.2"]
["318","1147501","error","LNodeType(SZNR_RREC_PRS713D)未被引用","DL/T1873","10.2"]
["319","1147520","error","LNodeType(SZNR_GAPC_PRS713D)未被引用","DL/T1873","10.2"]
["320","1147529","error","LNodeType(SZNR_GGIO_SPC48_PRS713D)未被引用","DL/T1873","10.2"]
["321","1147583","error","LNodeType(SZNR_GGIO_SPC80_PRS713D)未被引用","DL/T1873","10.2"]
["322","1147669","error","LNodeType(SZNR_GGIO_DPC16_PRS713D)未被引用","DL/T1873","10.2"]
["323","1147691","error","LNodeType(SZNR_PTRC_GOOSE_PRS7K0)未被引用","DL/T1873","10.2"]
["324","1147701","error","LNodeType(SZNR_CILO_CTR16_PRS713D)未被引用","DL/T1873","10.2"]
["325","1147725","error","LNodeType(SZNR_GGIO_SKYX_PRS713D)未被引用","DL/T1873","10.2"]
["326","1147763","error","LNodeType(SZNR_GAPC_SKYS_PRS713D)未被引用","DL/T1873","10.2"]
["327","1147778","error","LNodeType(SZNR_GAPC_SKRW_PRS713D)未被引用","DL/T1873","10.2"]
["328","1147788","error","LNodeType(SZNR_RSYN_PRS713D)未被引用","DL/T1873","10.2"]
["329","1147826","error","LNodeType(SZNR_GGIO_AnIn12_PRS7K)未被引用","DL/T1873","10.2"]
["330","1152806","error","DOType(SF_DPC_1)未被引用","DL/T1873","10.2"]
["331","1152867","error","DOType(SF_BlkCls_1)未被引用","DL/T1873","10.2"]
["332","1151457","error","DOType(CN_SPC0)未被引用","DL/T1873","10.2"]
["333","1153071","error","DOType(CN_WYE_ALL_EX)未被引用","DL/T1873","10.2"]
["334","1152261","error","DOType(SF_CMV_2)未被引用","DL/T1873","10.2"]
["335","1153228","error","DOType(J_ASG_0)未被引用","DL/T1873","10.2"]
["336","1151532","error","DOType(CN_INS_CBOpCap)未被引用","DL/T1873","10.2"]
["337","1153734","error","DOType(CN_ING_SP_EX1)未被引用","DL/T1873","10.2"]
["338","1151580","error","DOType(CN_MV3)未被引用","DL/T1873","10.2"]
["339","1153221","error","DOType(J_CMV_0)未被引用","DL/T1873","10.2"]
["340","1153667","error","DOType(CN_WYE_EX2)未被引用","DL/T1873","10.2"]
["341","1152407","error","DOType(CN_DPC_EX)未被引用","DL/T1873","10.2"]
["342","1152738","error","DOType(CN_BSC_EX)未被引用","DL/T1873","10.2"]
["343","1153159","error","DOType(J_INC_0)未被引用","DL/T1873","10.2"]
["344","1153232","error","DOType(CN_MV5)未被引用","DL/T1873","10.2"]
["345","1151397","error","DOType(CN_INS_SwOpCap)未被引用","DL/T1873","10.2"]
["346","1151474","error","DOType(CN_DPC0)未被引用","DL/T1873","10.2"]
["347","1153691","error","DOType(CN_DPC_SV_EX)未被引用","DL/T1873","10.2"]
["348","1153982","error","DOType(CN_CMV5)未被引用","DL/T1873","10.2"]
["349","1152943","error","DOType(SZNR_SAV)未被引用","DL/T1873","10.2"]
["350","1151431","error","DOType(CN_INC_Mod)未被引用","DL/T1873","10.2"]
["351","1151500","error","DOType(XJ_SPC)未被引用","DL/T1873","10.2"]
["352","1153744","error","DOType(CN_ASG_SG_EX4)未被引用","DL/T1873","10.2"]
["353","1152697","error","DOType(CN_ASG_SP_EX1)未被引用","DL/T1873","10.2"]
["354","1152453","error","DOType(SNR_INS_EX)未被引用","DL/T1873","10.2"]
["355","1152781","error","DOType(SF_WYE_20)未被引用","DL/T1873","10.2"]
["356","1153052","error","DOType(SZNR_ASG_SP_EX)未被引用","DL/T1873","10.2"]
["357","1153216","error","DOType(J_ING_0)未被引用","DL/T1873","10.2"]
["358","1153329","error","DOType(CN_CMV2)未被引用","DL/T1873","10.2"]
["359","1151387","error","DOType(CN_INS_SwTyp)未被引用","DL/T1873","10.2"]
["360","1152953","error","DOType(SZNR_WYE)未被引用","DL/T1873","10.2"]
["361","1153727","error","DOType(CN_SPG_SP_EX0)未被引用","DL/T1873","10.2"]
["362","1153556","error","DOType(CN_SPS_NSV_EX)未被引用","DL/T1873","10.2"]
["363","1152688","error","DOType(CN_ASG_SP1)未被引用","DL/T1873","10.2"]
["364","1153064","error","DOType(SF_WYE_2NA0)未被引用","DL/T1873","10.2"]
["365","1151437","error","DOType(CN_BSC)未被引用","DL/T1873","10.2"]
["366","1152773","error","DOType(SF_MV_10)未被引用","DL/T1873","10.2"]
["367","1151514","error","DOType(CN_LPL_LN00)未被引用","DL/T1873","10.2"]
["368","1152329","error","DOType(SF_ING_1EX)未被引用","DL/T1873","10.2"]
["369","1151491","error","DOType(CN_SAV)未被引用","DL/T1873","10.2"]
["370","1151522","error","DOType(XJ_SAV_EX)未被引用","DL/T1873","10.2"]
["371","1152787","error","DOType(SF_WYE_2NA)未被引用","DL/T1873","10.2"]
["372","1152903","error","DOType(SZNR_CN_SAV)未被引用","DL/T1873","10.2"]
["373","1153182","error","DOType(J_SPC_0)未被引用","DL/T1873","10.2"]
["374","1153210","error","DOType(J_MV_1)未被引用","DL/T1873","10.2"]
["375","1153607","error","DOType(CN_MV_NSV_EX)未被引用","DL/T1873","10.2"]
["376","1152963","error","DOType(SZNR_SPC_NSV_EX)未被引用","DL/T1873","10.2"]
["377","1153578","error","DOType(CN_INS_ARST0)未被引用","DL/T1873","10.2"]
["378","1153825","error","DOType(CN_MV_EX4)未被引用","DL/T1873","10.2"]
["379","1151421","error","DOType(CN_INS)未被引用","DL/T1873","10.2"]
["380","1152268","error","DOType(SF_DPC_3)未被引用","DL/T1873","10.2"]
["381","1152925","error","DOType(SZNR_CMV_SV)未被引用","DL/T1873","10.2"]
["382","1153196","error","DOType(J_SPS_1)未被引用","DL/T1873","10.2"]
["383","1152897","error","DOType(SZNR_INS_NSV)未被引用","DL/T1873","10.2"]
["384","1152636","error","DOType(CN_SPG_SG)未被引用","DL/T1873","10.2"]
["385","1152729","error","DOType(CN_SAV3)未被引用","DL/T1873","10.2"]
["386","1152472","error","DOType(CN_ACT_EX0)未被引用","DL/T1873","10.2"]
["387","1152873","error","DOType(SF_CBOpCap_1)未被引用","DL/T1873","10.2"]
["388","1153470","error","DOType(CN_DEL_EX0)未被引用","DL/T1873","10.2"]
["389","1152801","error","DOType(SF_OpCnt_1)未被引用","DL/T1873","10.2"]
["390","1152719","error","DOType(SNR_LPL_EX)未被引用","DL/T1873","10.2"]
["391","1153660","error","DOType(CN_WYE3)未被引用","DL/T1873","10.2"]
["392","1152848","error","DOType(SF_ASG_2EX0)未被引用","DL/T1873","10.2"]
["393","1151377","error","DOType(CN_SPS0)未被引用","DL/T1873","10.2"]
["394","1151407","error","DOType(CN_MV0)未被引用","DL/T1873","10.2"]
["395","1152822","error","DOType(SF_SwOpCap_1)未被引用","DL/T1873","10.2"]
["396","1153005","error","DOType(SZNR_SPG_SG_EX)未被引用","DL/T1873","10.2"]
["397","1153597","error","DOType(CN_ACD_Simple_EX)未被引用","DL/T1873","10.2"]
["398","1152761","error","DOType(CN_SAV_EX1)未被引用","DL/T1873","10.2"]
["399","1152594","error","DOType(CN_DPC_EX0)未被引用","DL/T1873","10.2"]
["400","1152075","error","DOType(CN_SPC2)未被引用","DL/T1873","10.2"]
["401","1152817","error","DOType(SF_SwTyp_1)未被引用","DL/T1873","10.2"]
["402","1153565","error","DOType(CN_SPS_SV_EX)未被引用","DL/T1873","10.2"]
["403","1152109","error","DOType(CN_SAV2)未被引用","DL/T1873","10.2"]
["404","1152494","error","DOType(CN_MV_EX1)未被引用","DL/T1873","10.2"]
["405","1153177","error","DOType(J_DPL_0)未被引用","DL/T1873","10.2"]
["406","1152827","error","DOType(SF_SPC_1DO)未被引用","DL/T1873","10.2"]
["407","1153674","error","DOType(CN_WYE_ALL1)未被引用","DL/T1873","10.2"]
["408","1152676","error","DOType(CN_ASG_SG_EX1)未被引用","DL/T1873","10.2"]
["409","1151558","error","DOType(CN_MV2)未被引用","DL/T1873","10.2"]
["410","1152548","error","DOType(CN_DEL_EX)未被引用","DL/T1873","10.2"]
["411","1153022","error","DOType(SZNR_ASG_SG)未被引用","DL/T1873","10.2"]
["412","1153031","error","DOType(SZNR_ASG_SG_EX)未被引用","DL/T1873","10.2"]
["413","1153246","error","DOType(CN_INS2)未被引用","DL/T1873","10.2"]
["414","1152310","error","DOType(SF_SPC_2)未被引用","DL/T1873","10.2"]
["415","1152884","error","DOType(SZNR_SPS_SV)未被引用","DL/T1873","10.2"]
["416","1153684","error","DOType(CN_DEL_EX1)未被引用","DL/T1873","10.2"]
["417","1153775","error","DOType(CN_INC_NSV)未被引用","DL/T1873","10.2"]
["418","1152296","error","DOType(SF_SPC_1EX)未被引用","DL/T1873","10.2"]
["419","1152912","error","DOType(SZNR_CN_SAV_EX)未被引用","DL/T1873","10.2"]
["420","1153643","error","DOType(CN_CMV_NSV_EX)未被引用","DL/T1873","10.2"]
["421","1152440","error","DOType(CN_INS_EX1)未被引用","DL/T1873","10.2"]
["422","1152538","error","DOType(CN_WYE_EX)未被引用","DL/T1873","10.2"]
["423","1153043","error","DOType(SZNR_ASG_SP)未被引用","DL/T1873","10.2"]
["424","1153165","error","DOType(J_INS_0)未被引用","DL/T1873","10.2"]
["425","1152251","error","DOType(SF_CMV_1EX)未被引用","DL/T1873","10.2"]
["426","1153170","error","DOType(J_LPL_0)未被引用","DL/T1873","10.2"]
["427","1151507","error","DOType(XJ_DPC)未被引用","DL/T1873","10.2"]
["428","1152207","error","DOType(SF_WYE_1)未被引用","DL/T1873","10.2"]
["429","1152667","error","DOType(CN_ASG_SG1)未被引用","DL/T1873","10.2"]
["430","1152835","error","DOType(SF_ASG_1EX0)未被引用","DL/T1873","10.2"]
["431","1153435","error","DOType(CN_CMV3)未被引用","DL/T1873","10.2"]
["432","1152213","error","DOType(SF_WYE_1EX)未被引用","DL/T1873","10.2"]
["433","1152861","error","DOType(SF_BlkOpn_1)未被引用","DL/T1873","10.2"]
["434","1152979","error","DOType(SZNR_SPC_DC)未被引用","DL/T1873","10.2"]
["435","1151665","error","DOType(XJ_CMV)未被引用","DL/T1873","10.2"]
["436","1152794","error","DOType(SF_CMV_20)未被引用","DL/T1873","10.2"]
["437","1152092","error","DOType(CN_DPC1)未被引用","DL/T1873","10.2"]
["438","1152513","error","DOType(CN_CMV1)未被引用","DL/T1873","10.2"]
["439","1152531","error","DOType(CN_WYE1)未被引用","DL/T1873","10.2"]
["440","1152244","error","DOType(SF_CMV_1)未被引用","DL/T1873","10.2"]
["441","1153622","error","DOType(CN_CMV_SV_EX)未被引用","DL/T1873","10.2"]
["442","1153711","error","DOType(CN_DPC_NSV)未被引用","DL/T1873","10.2"]
["443","1153917","error","DOType(XJ_SAV_EX1)未被引用","DL/T1873","10.2"]
["444","1152988","error","DOType(SZNR_DPC_SV)未被引用","DL/T1873","10.2"]
["445","1153012","error","DOType(SZNR_ING_SG_EX)未被引用","DL/T1873","10.2"]
["446","1152614","error","DOType(CN_INC_EX)未被引用","DL/T1873","10.2"]
["447","1153588","error","DOType(CN_ACT_Simple_EX)未被引用","DL/T1873","10.2"]
["448","1153844","error","DOType(CN_CMV4)未被引用","DL/T1873","10.2"]